## Disclaimer
DISCLAIMER
REPORTING OF BUGS
If you find any bug in the tool please report it in this email: jaspersnetwork@eib.org using "Excel tools bug reporting" as subject
Version December 2024
This tool has been designed for small projects and is provided in good faith, to be used at the risk of the user under its responsibility.
EIB Advisory JASPERS does not warrant the accuracy or completeness of the information and assessment performed with this tool nor does it assume any legal liability or responsibility, direct or indirect, for any damages or loss caused or alleged to be caused by or in connection with the use of or reliance on information contained in this tool.
This tool has not been formally discussed or approved by the European Commission. The assessment resulting from the use of the tool does not necessarily state or reflect the views of the EIB Advisory JASPERS partners (European Commission and the European Investment Bank (EIB).
EIB retains copyright to this tool on behalf of EIB Advisory JASPERS. Permission to distribute this tool in whole for non-commercial purposes and without fee is hereby granted provided that EIB Advisory JASPERS is acknowledged.
The tool performs a simplified likelihood analysis that considers the probability of experiencing the most severe hazard in the project location. .It uses an indicator-based approach for the characterisation of potential climate hazards and risks, that is simple albeit subjective. It relies on empirical evidence and hence can be applied by non-climate experts. It does not however entail the robustness of a quantitative risk analysis which evaluates losses on exposed elements using probabilistic metrics.
The tool has been developed in MS Excel and it has not been tested in other spreadsheet applications so it might not work properly with other applications.
DEFINITION OF SMALL-SCALE PROJECTS
The definition of small-scale projects is subject to variations based on country-specific context and regulation and should be defined by the National Managing Authorities.
JASPERS recommendation for small water, wastewater and irrigation projects that could use this Excel tool is provided below. For larger projects a climate resilience assessment following the methodology in the EC "Technical guidance on the climate proofing of infrastructure in the period 2021-2027" is recommended.

## Intro
HOW TO USE THE CLIMATE-PROOFING TOOL
GETTING STARTED
Before starting the climate-proofing exercise go through the technical documentation of the project. What are the key functions of the project? Which assets are involved in the various processes? Which technical specifications have been incorporated in their design?
Make a list of all processes and assets. How does the different components interact with each other (input - output) and how do they interact with the external environment? How reliant is the project to other infrastructure systems (i.e., power and transport network) for performing its function?
ANALYSIS
The analysis is performed in four cycles representing four broad classes of hazards as displayed in the sketch below. Each hazard class may include more than one hazards.
The analysis flow is common to all hazards. It commences with the estimation of hazard exposure (Step 1), it continues with the assessment of sensitivities in Step 2 (discriminating between the various project assets and processes), followed by a preliminary risk assessment (Step 3) describing the risk level of the different project components to various hazards considered. In Step 4 the user specifies adaptation measures for the most vulnerable project components and re-calculates the residual risk of the project (meaning the climate risk after the implementation of the specified adaptation measures.
The climate proofing assessment is completed when the residual risk is lower than a maximum acceptable risk level. Note that the characterization of "acceptable risk" may differ among the various components and processes. For critical/valuable processes/assets, this can be set to Low. For less critical asset/components a "Medium" acceptable risk may be also admissible.
OUTPUT
A climate risk overview of the project (before and after the implementation of adaptation measures).
A list of suitable adaptation measures for the various hazards considered.
HAZARD EXPOSURE
Water-related
hazards
Temperature-related hazards
Soil-related
hazards
STEP 01
STEP 02
STEP 04
STEP 03
STEP 01
STEP 02
STEP 03
STEP 04
STEP 01
STEP 02
STEP 03
STEP 04
Output
HAZARD EXPOSURE
SENSITIVITY ASSESSMENT
RISK ASSESSMENT
ADAPTATION MEASURES
(for water-related hazards)
HAZARD EXPOSURE
SENSITIVITY ASSESSMENT
RISK ASSESSMENT
ADAPTATION MEASURES
(for temperature-related hazards)
SENSITIVITY ASSESSMENT
RISK ASSESSMENT
ADAPTATION MEASURES
(for soil-related hazards)
Extreme
winds
STEP 01
STEP 02
STEP 03
STEP 04
HAZARD EXPOSURE
SENSITIVITY ASSESSMENT
RISK ASSESSMENT
ADAPTATION MEASURES
(for extreme winds)

## Water-Step 1
Climate-proofing of Water & Wastewater Projects against water-related hazards
STEP 1. RATE EXPOSURE combined with likelihood of occurrence
Table 1.1. Exposure to Flood
Flood exposure describes the proneness of a region to experience fluvial and pluvial flooding. To determine flood exposure users may contact national databases and advise flood hazard maps or flood risk maps for the area of interest. If such maps are not available, the exposure to flood events may be determined empirically answering the list of questions described below.
Select one option from the drop-down menu
| How will the assessment be performed? | Empirical Indicators
Fill-in the white cells
| Question | Instructions | [0] | [1] | [2] | [3] | Provide a score from [0 to 3]
|  |  | NO | LIKELY | MOST LIKELY | YES
| 0 | 0
Q1.1 | Is the project constructed on a floodplain, wetland or a low-lying barrier? | These are flat areas that are close to waterfront (lake or sea). Because of their modest elevation (no more than 10 m) such areas are prone to flooding and storm surges. | 0 |  |  | 3
Q1.2 | Is the project developed along riverside? | During severe strorms, rivers and streams may overflow covering riverside areas of low elevation. Moreover, high river flows may cause river banks to collapse causing severe damage to riverside developments and infrastructure. | 0 |  |  | 3
Q1.3 | Has the area experienced significant flooding in recent history? | Answer 'YES' if a major flood event has occurred over the past 50-years; Answer 'NO' if there is no recent memory of a major flood event in the region. | 0 |  |  | 3
Q1.4 | Do any of the access routes of the project fall within a floodplain? | Even if the facility remains intact, flooding may hamper accessibility impacting the supply chain or the transportation of people to/from the project. | 0 | 1 | 2 | 3
* if your response is positive, answer also 'YES' to Questions Q1.2 and Q1.3
** if your response is positive, answer also 'YES' to Question Q1.3
[5 empty] | Current Flood Score: |  | #DIV/0!
[5 empty] | Current Flood Risk: |  | #DIV/0!
| Table 1.2. Exposure to Drought | [5 empty] | Fill-in the white cells
| Question | Instructions | [0] | [1] | [2] | [3] | Provide a score from [0 to 3]
|  |  | NO | LIKELY | MOST LIKELY | YES
Q1.5 | Has the region experienced periods of increased droughts during the past years? | Droughts are prolonged periods of very low precipitation resulting in water shortage. Answer 'YES' if the most recent drought event is no more than 25 years old, 'Most likely' if it is between 25-50 years, 'Likely' if it is more than 50 years, 'NO' if the region has experienced no serious drought events in the past. | 0 | 1 | 2 | 3
Q1.6 | Has the region recently experienced critically low level of water in lakes, streams and reservoirs? | Answer 'YES' if water shortages are widespread and water restrictions have been imposed, 'Most likely' if water shortages are common, 'Likely' if water shortages are imminent, 'No' in all other cases. | 0 | 1 | 2 | 3
Q1.7 | Has the region recently experienced crop or pasture loss? | Answer 'YES' if 'crop/pasture losses are major, 'Most likely' if crop/pasture losses are likely, 'Likely' if some crop/pasture damages have been observed, 'No' in all other cases. | 0 | 1 | 2 | 3
[5 empty] | Current Drought Score: |  | 0
[5 empty] | Current Drought Risk: |  | Low
Select one option from the drop-down menu
| Is the project located at a coastal site? | NO | If NO, continue to Q1.12
| Table 1.3. Exposure to Coastal flooding, Sea-level rise and Storm surge | [5 empty] | Fill-in the white cells
| Question | Instructions | [0] | [1] | [2] | [3] | Provide a score from [0 to 3]
|  |  | NO | LIKELY | MOST LIKELY | YES
Q1.8 | Is the project constructed on a sandy coastline? Has the land space of the shore substantially compressed during the past 50 years? | Answer 'YES' if there are clear indications that the coast has been shrinking; 'No' if there are no oblivious changes in the coastal boundary over the past 50 years. | 0 |  |  | 3
Q1.9 | Is it common for the project area to be impacted by high-tides and destructive waves created by strong winds? | Answer 'YES' if hugh tides are a common threat (and the coastal protection is insufficient), 'Most likely' if the area is protected by a natural buffer (e.g. coastal dunes or a marsh estuary) that slow down overland flow of stormwater offering some sort of protection, 'Likely' if the area is coastal protected (by any combination of engineered ana nature-based solutions); 'No' if the area is not exposed to high tides or destructive waves. | 0 | 1 | 2 | 3
Q1.10 | Has the dunefield of the area changed over the past 20 years? | As the wave action is erroding the shoreline, and the wind is carrying sand inland more dunes are expected to be formed in the backshore. A landward migration of dunes is common in regions suffering from storm surge impacts and coastal erosion. Sea-level rise will most likely accelerate the trends. | 0 |  |  | 3
Q1.11 | Is the project located on a soft coastal cliff? | Answer 'YES' if the project is located on soft coastal cliff that experiences frequent collapses of earth and rock masses, severe cracking and cave formation (signs of coastal erosion and sea-level rise); 'NO' in al other cases. | 0 |  |  | 3
[5 empty] | Coastal flooding score: |  | 0
[5 empty] | Coastal flooding risk: |  | Low
| Table 1.4. Exposure to impaired water quality | [5 empty] | Fill-in the white cells
| Question | Instructions | [0] | [1] | [2] | [3] | Provide a score from [0 to 3]
|  |  | NO | LIKELY | MOST LIKELY | YES
Q1.12 | Is the service area of the facility characterized by intensified agricultural activity? | Soils in areas of increased agricultural activity are commonly rich in PFAS1. Accumulation of contaminated sediments in nearby reservoirs will potentially impair their capacity to provide drinking water. | 0 |  |  | 3
Q1.13 | Have previous floods events transported soils/sediments/organic matter to the water intake of the facility (river or lake)? | Answer 'YES' if ' reservoir sedimentation is common (and dredging activities are therefore regular); 'Most likely' if there are circumstances of soil sedimentation (or if an aggravation of sedimentation rate is expected to occur); Likely if sedimentation is imminent (e.g., reservoirs surrounded by overcultivated lands), 'No' in all other cases. | 0 | 1 | 2 | 3
Q1.14 | Is it common for the catchment area to experience flash floods and surface run-off when it rains? | Water run-off is a condition where the rainwater does not infiltrate into the ground but flows unconfined over the ground surface. This is most common in arid regions, with low vegetation and high inclinations. | 0 |  |  | 3
1 Per- and polyfluoroalkyl substances
[5 empty] | Water contamination Score: |  |  | 0
[5 empty] | Water contamination Level : |  |  | Low
| Climate Change Projections | [9 empty] | `
(1) Consult the regional climate projections IPCC Interactive Atlas (https://interactive-atlas.ipcc.ch) to determine how precipitation patterns, floods, ans sea-level will change due to climate change. (2) Specify a climate-change multiplier [from 0.8 to 1.5] that will be used for the estimation of future exposure levels. Base your response on the trajectory of the change (increasing or decreasing) and the associated confidence level (Low, Medium, High). If the trajectory of change is stable set the climate-change multiplier equal to 1.0. Where available, consult downscaled climate projections to refine your answer.
| Table 1.5. Climate projections for flood risk | [7 empty] | Fill-in the white cells
| Question | Instructions | Decreasing trend |  |  | Increasing trend |  |  | Climate-change multiplier
|  |  | Low Confidence | Medium Confidence | High Confidence | Low Confidence | Medium Confidence | High Confidence
Q1.15 | All sites: Will the region experience heavier and more frequent storms in the future? Are the trends increasing or decreasing? | Obtain the regional projections by IPCC for heavy precipitation to estimate the climate-change multiplier. | 1 | 0.9 | 0.8 | 1.2 | 1.3 | 1.5
Q1.16 | Low-lying regions closed to river and lakes: Is the risk of river flooding expected to increase? | Obtain the regional projections by IPCC for river flooding to estimate the climate-change multiplier. | 1 | 0.9 | 0.8 | 1.2 | 1.3 | 1.5
[5 empty] | Future flood score: |  | #DIV/0!
[5 empty] | Future flood risk: |  | #DIV/0!
| Table 1.6. Climate projections on drought conditions | [7 empty] | Fill-in the white cells
| Question | Instructions | Decreasing trend |  |  | Increasing trend |  |  | Climate-change multiplier
|  |  | Low Confidence | Medium Confidence | High Confidence | Low Confidence | Medium Confidence | High Confidence
Q1.17 | Is the risk of drought expected to increase? | Obtain the regional projections by IPCC for aridity to estimate the climate-change multiplier. If not available, base your response on mean annual projections of temperature/precipitation (i.e., drought conditions are expected to increase, if mean temperature increases and precipitation averages decrease concurrently). | 1 | 0.9 | 0.8 | 1.2 | 1.3 | 1.5
Q1.18 | How will climate change affect annual average precipitation patterns? Is the mean annual precipitation expected to decrease? | Obtain the regional projections by IPCC for mean precipitation to estimate the respective climate-change multiplier2. | 1 | 0.9 | 0.8 | 1.2 | 1.3 | 1.5
| 2 Alternatively approach for experienced users: Consult the national climate-change database and assign a score to the climate-change multiplier based on the magnitude of change of total annual precipitation (or the rate of change of total annual precipitation) for a considered climate scenario and time horizon. | [8 empty] | `
[5 empty] | Future drought score: |  | 0
[5 empty] | Future drought risk: |  | Low
| Table 1.7. Climate projections on coastal flooding, sea-level rise and storm surge | [7 empty] | Fill-in the white cells
| Question | Instructions | Decreasing trend |  |  | Increasing trend |  |  | Climate-change multiplier
|  |  | Low Confidence | Medium Confidence | High Confidence | Low Confidence | Medium Confidence | High Confidence
Q1.19 | Is the risk of coastal flooding expected to increase? | Obtain the regional projections by IPCC for coastal flooding to estimate the respective climate-change multiplier3. | 1 | 0.9 | 0.8 | 1.2 | 1.3 | 1.5
Q1.20 | Is the sea level expected to rise up over the next years ? | Obtain the regional projections by IPCC for relative sea level to estimate the respective climate-change multiplier. | 1 | 0.9 | 0.8 | 1.2 | 1.3 | 1.5
Q1.21 | Is coastal erosion expected to intensify? | Obtain the regional projections by IPCC for coastal erosion to estimate the respective climate-change multiplier. | 1 | 0.9 | 0.8 | 1.2 | 1.3 | 1.5
[5 empty] | Future sea-level score: |  | 0
[5 empty] | Future sea-level rise risk: |  | Low
[5 empty] | Future contamination score: |  | 0
[5 empty] | Future contamination risk: |  | Low
Instructions
This step will help users rate the susceptibility of the project area to flooding, drought, sea-level rise and impaired water conditions considering present and future climate conditions.
CURRENT EXPOSURE
1. Exposure to flooding: Select the type of assessment. The assessment can be semi-qualitative using available maps, or purely qualitatively using empirical indicators. The selection is a matter of user preference and relies on the type of available data. Inexperienced users are advised to use the ‘Empirical Indicators’ option.
2.Determine whether the conditions described in Table1.1 apply to the area of interest. Fill-in only the non-shaded cells. The flood exposure score will automatically appear in the highlighted cell.
3. Answer the questions of Tables 1.2 and 1.4 to assess the (current) exposure to drought, sea-level rise and impaired water. The exposure score will automatically appear in the respective highlighted cells.
FUTURE PROJECTIONS
4. Look up the regional climate projections of IPCC (https://interactive-atlas.ipcc.ch) and observe how the rainfall patterns and flooding conditions are expected to change in the future.
5. Follow the probe Questions of Table 1.5 to define a climate-change multiplier for each condition described. Set the multiplier > 1 if the trends are increasing (i.e., the region is expected to experience heavier flooding), and < 1 in case milder climate conditions are expected to materialize. The updated exposure level to flooding (representative for future climate conditions) will be automatically calculated by multiplying the current exposure with the climate-change multiplier.
6. Assign a climate-change multiplier for the remaining hazrds following the probe questions of Tables 1.6 and 1.7. As previously, the future exposure to the above hazards will be automatically displayed in the respective highlighted cells.
7. The maximum exposure scores (current or future) for each hazard will be transferred to Step 3 to inform the Preliminary Risk Assessment.
DEFINITION OF EXPOSURE LEVEL
NOTE
Set equal to 0.0 if the project is not located at a low-lying region
HOW TO USE THE IPCC INTERACTIVE ATLAS to estimate a climate-change multiplier
1. Follow the link : https://interactive-atlas.ipcc.ch 2. Choose Regional Sythesis 3. At the top left corner of the page, select the tab 'Regions' 4. Go to 'Europe' Section and specify the regional subsystem that applies to the project under consideration. 5. The regional climate projections will be appear on the right. Browse the inofrmation provided, to obtain the future trend of the requested climate stressor.
NOTE
Leave blank, if the project is not located at a coastal site.

## Water-Step 2
Climate-proofing of Water & Wastewater Projects against water-related hazards
STEP 2. RATE SENSITIVITY combining impacts and in-built adaptive capacity
|  |  | Use the drop-down menu to select type of the project: | Wastewater Collection & Treatment
Table 2.1. Component-based sensitivity assessment to water-related hazards
| Components Selection |  |  | Sensitivity to Heavy Precipitation & Flooding | [5 empty] | Adaptive Capacity to Heavy Precipitation & Flooding |  |  |  | Flooding Score |  |  | Continue the assessment for Drought conditions |  |  | Sensitivity to Drought |  |  |  |  | Adaptive Capacity to Drought |  |  | Drought Score |  |  | Continue the assessment for sea-level rise and storm surge |  |  | Sensitivity to sea-level rise and storm surge | [5 empty] | Adaptive Capacity to sea-level rise and storm surge |  |  |  | Sea-level rise score |  |  | Continue the assessment for impaired water conditions |  |  | Sensitivity to impaired water conditions |  |  |  |  | Adaptive Capacity to impaired water conditions |  |  | Impaired water conditions score
|  |  | 0 | Provide your score in the white cells | [5 empty] | Provide your score in the white cells | [9 empty] | Provide your score in the white cells |  |  |  |  | Provide your score in the white cells | [8 empty] | Provide your score in the white cells | [5 empty] | Provide your score in the white cells | [9 empty] | Provide your score in the white cells |  |  |  |  | Provide your score in the white cells
|  |  |  | Q2.1 | Q2.2 | Q2.3 | Q2.4 |  |  | Q2.5 | Q2.6 | Q2.7 | [7 empty] | Q2.8 | Q2.9 | Q2.10 |  |  | Q2.11 | Q2.12 | Q2.13 | [6 empty] | Q2.14 | Q2.15 | Q2.16 | Q2.17 |  |  | Q2.18 | Q2.19 | Q2.20 | Q2.21 | [6 empty] | Q2.22 | Q2.23 | Q2.24 |  |  | Q2.25 | Q2.26 | Q2.27
| Select N/A from the drop-down menu to de-activate components that do not apply to the project under consideration |  |  | Based on past experience, will the component remain functional (or sustain minimum damage) in the event of a flood? | Is the component protected from storm and flood water (e.g., use of flood gates/barriers)? | Can the component withstand/accommodate increased water flows? (e.g., through the use of larger pipe sections, enahnced drainage system etc) | Can the component impede/divert increased water flows (e.g. through the use of overflow tanks, emergency spillways)? | Average Sensitivity Score | Component Sensitivity | Have any of the adaptation measures (listed in Tables 4.2 and 4.3 of Step 4) been included in the design of the specific component? | Are there redundancies that could reduce impacts in case the component/process fails? (e.g., process by-passing, available pump stock, alternative access routes, Emergency Power Generators) | In case of failure, can the component (or its performed function) be quickly replaced/ (restored)? | Final Sensitivity Score |  | Final Sensitivity Level |  |  |  |  | Based on past experience will the asset/process be affected in prolonged drought periods? | Is the performance affected by the wastewater quality? | Can the component adapt to input/output changes (e.g., changes in water flow or water availability) ? | Average Sensitivity Score | Component Sensitivity | Have any of the adaptation measures (listed in Tables 4.2 and 4.3 of Step 4) been included in the design of the specific component? | Are there redundancies that could reduce impacts in case the asset/process fails? | Is there a water-shortage contingency plan (e..g alternate water resources, water-conservation management approaches)? | Final Sensitivity Score | Final Sensitivity Level |  |  |  |  | Based on past experience, will the component remain functional (or sustain minimum damage) in case of high-tide conditions? | Is the component water-resistant (i.e., maintains its functionality when exposed to compound flooding or when completely inundated)? | Can the component withstand increased wave actions? | Can the component impede or divert increased water flows (e.g. using drains, pumps, flood gates/barriers)? | Average Sensitivity Score | Component Sensitivity | Have any of the adaptation measures (listed in Table 4.2 of Step 4) been included in the design of the specific component? | Are there redundancies that could reduce impacts in case the component fails? | In case of failure, can the component be quickly replaced (or its performed function restored)? | Can the component operate using low-quality wastewater? | Final Sensitivity Score | Final Sensitivity Level |  |  |  |  | Based on past experience, has the component ever been exposed to impaired water conditions yet continued to operate? Leave blank if there are no precedents of exposure to impaired water. | Is the component protected from impaired water conditions (e.g., pre-processing, control technologies) | How much is the component's performance affected by the wastewater quality? | Average Sensitivity Score | Component Sensitivity | Have any of the adaptation measures (listed in Tables 4.2 and 4.3 of Step 4) been included in the design of the specific component? | In case of failure, can the asset/process be quickly replaced/by-passed? | Can the component adapt to input/output changes (e.g., contamination level of effluent) ? | Final Sensitivity Score | Final Sensitivity Level
| COMPONENT | SELECTION | POSSIBLE FAILURE MODES | [0: Yes ¦ 3: No] | [0: Yes ¦ 1: Most Likely ¦ 2: Likely ¦ 3: No] | [0: Yes ¦ 1: Most Likely ¦ 2: Likely ¦ 3: No] | [0: Yes ¦ 1: Most Likely ¦ 2: Likely ¦ 3: No ] | [0 - 3] | [Low ¦ Medium ¦ High] | [3: Yes, more than one measure of high efficiency, 2: Yes, at least one measure of high efficiency ¦ 1: Yes, at least one measure of low efficiency¦ 0: No adaptation measures] | [3: Yes ¦ 2: Most Likely ¦1: Likely ¦ 0: No ] | [3: Yes ¦ 2: Most Likely ¦ 1: Likely ¦ 0: No ] | [0-3] |  | [Low ¦ Medium ¦ High] |  | COMPONENT | SELECTION | POSSIBLE FAILURE MODES | [0: No ¦ 3: Yes ] | [0: Minimal ¦ 1: Moderately ¦ 2: Substantially ¦ 3:Excessively ] | [0: Yes ¦ 1: Most Likely ¦ 2: Likely ¦ 3: No ] | [0 - 3] | [Low ¦ Medium ¦ High] | [3: Yes, more than one measure of high efficiency, 2: Yes, at least one measure of high efficiency ¦ 1: Yes, at least one measure of low efficiency¦ 0: No adaptation measures] | [3: Yes ¦ 2: Most Likely ¦ 1: Likely ¦ 0: No ] | [3: Yes ¦ 2: Most Likely ¦1: Likely ¦ 0: No ] | [0-3] | [Low ¦ Medium ¦ High] |  | COMPONENT | SELECTION | POSSIBLE FAILURE MODES | [0: Yes ¦ 3: No] | [0: Yes ¦ 1: Most Likely ¦ 2: Likely ¦ 3: No] | [0: Yes ¦ 1: Most Likely ¦ 2: Likely ¦ 3: No] | [0: Yes ¦ 1: Most Likely ¦ 2: Likely ¦ 3: No ] | [0 - 3] | [Low ¦ Medium ¦ High] | [3: Yes, more than one measure of high efficiency, 2: Yes, at least one measure of high efficiency ¦ 1: Yes, at least one measure of low efficiency¦ 0: No adaptation measures] | [3: Yes ¦ 2: Most Likely ¦ 1: Likely ¦ 0: No ] | [3: Yes ¦ 2: Most Likely ¦ 1: Likely ¦ 0: No ] | [3: Yes ¦ 2: Most Likely ¦ 1: Likely ¦ 0: No ] | [0-3] | [Low ¦ Medium ¦ High] |  | COMPONENT | SELECTION | POSSIBLE FAILURE MODES | [ 0: Yes; 3:No ] | [0: Yes ¦ 1: Most Likely ¦ 2: Likely ¦ 3: No ] | [0: Minimal ¦ 1: Moderately ¦ 2: Substantially ¦ 3:Excessively ] | [0 - 3] | [Low ¦ Medium ¦ High] | [3: Yes, more than one measure of high efficiency, 2: Yes, at least one measure of high efficiency ¦ 1: Yes, at least one measure of low efficiency¦ 0: No adaptation measures] | [3: Yes ¦ 2: Most Likely ¦ 1: Likely ¦ 0: No ] | [3: Yes ¦ 2: Most Likely ¦ 1: Likely ¦ 0: No ] | [0-3] | [Low ¦ Medium ¦ High]
Assets, processes, inputs & outputs | Sewerage networks and pumping stations | Active | Episodic peak flows exceeding the capacity of the sewerage system; Bypassing of treatment; Damaged/cracked mains and laterals caused by uneven settlements; Scouring of riverbanks at discharge outlets; Wastewater backflows into properties. |  |  |  |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! |  | #DIV/0! | Assets, processes, inputs & outputs | Sewerage networks and pumping stations | Active | N/A |  |  |  | N/A | N/A |  |  |  | N/A | N/A | Assets, processes, inputs & outputs | Sewerage networks and pumping stations | Active | Changes in the groundwater table could be responsible for significant ground deformations impacting the integrity of buried pipelines; Coastal piping systems and their associated components such as pump, shafts, and valves could suffer from severe erosion–corrosion in their metal parts (e.g. valve seats, pump impellers, and pump casings) leading to higher failure rates. |  |  |  |  | #DIV/0! | #DIV/0! |  |  | N/A |  | #DIV/0! | #DIV/0! | Assets, processes, inputs & outputs | Sewerage networks and pumping stations | Active | Faster corrosion of pipes transferring 'high-strength waste-water' (i.e., high in solids and pollutants); Changes in the flow rates and wastewater concentrations could affect the scouring effect and the sedimentation process generating unpleasant odors; Higher pumping capacity may be required to prevent low-flow conditions. |  |  |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | #DIV/0!
| Wastewater treatment plants and processes | Active | `1. Heavy rainfalls could increase the inflow of the Wastewater treatment plants and by extension could decrease the dilution ratio of the infuent. Such a decrease may affect the biological treatment processes and ultimately the quality of the effluent. 2. Flood events can also create severe structural damage to tanks, screens, and all sorts of valuable equipment; 3. During extreme weather, system bypasses can be activated, diverting flows past part or all of the treatment process. |  |  |  |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! |  | #DIV/0! |  | Wastewater treatment plants and processes | Active | Drought conditions reduce the amount of water that flows into the wastewater treatment; An increased occurrence of low flows could lead to decreased contaminant dilution capacity and higher pollutant concentrations resulting in blockages and early system corrosion. |  |  |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | #DIV/0! |  | Wastewater treatment plants and processes | Active | Severe structural damage of coastal plants (damaged tanks, pipes, etc) caused by tidal waves and compound flooding; Significant repair or protection works,(Risk of permanent shut-down or abandonment of stranded assets of located across the storm surge zone. |  |  |  |  | #DIV/0! | #DIV/0! |  |  | N/A |  | #DIV/0! | #DIV/0! |  | Wastewater treatment plants and processes | Active | Low-quality effluent requiring advanced/expensive treatment; Intensified bacterial growth requiring specialized treatment (e.g., extended use of chemical additives; two-staged treatment); Faster degradation/clogging of membranes/filters. |  |  |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | #DIV/0!
| Receiving river body | Active | Episodic peak flows leading to uncontrolled flow of untreated wastewater into receiving water bodies |  |  |  |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! |  | #DIV/0! |  | Receiving river body | Active | Low-quality effluent entering fresh water bodies (as a result of reduced dilution at low flow conditions). |  |  |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | #DIV/0! |  | Receiving river body | Active | Rising receiving-water levels reduce the outflow capacity of the facility; coastal plants may need to change from gravity to pumped effluent thereby increasing energy requirements. |  |  |  |  | #DIV/0! | #DIV/0! |  |  |  |  | #DIV/0! | #DIV/0! |  | Receiving river body | Active | Low-quality effluent entering freshwater bodies potentially impairing the water quality below acceptable standards (depending on the assimilative capacity of the watercourse or lake) |  |  |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | #DIV/0!
| Reuse of treated effluent for irrigation/recharge of aquifer | Active | Seasonal changes in the precipitation pattern may change the demand for irrigation water; an increase in the annual rainfall will lead to higher groundwater levels and will reduce the need fot aquuifer recharging. |  | N/A | N/A | N/A | #DIV/0! | #DIV/0! |  |  | N/A | #DIV/0! |  | #DIV/0! |  | Reuse of treated effluent for irrigation/recharge of aquifer | Active | Prolonged drought may create ‘high-strength wastewater’ effluent (characterized by higher concentrations in pollutants and pathogens); Risk of health issues if this low-qualaity effluent enters the acquifers or being used for irrigation. |  | N/A |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | #DIV/0! |  | Reuse of treated effluent for irrigation/recharge of aquifer | Active | Could significantly alter the land available for irrigation and hence irrigation demand; Saltwater-intrusion (driven by sea-water rise) may increase the toxicity of effluent beyond allowable standards; unsuitable irrigation water could reduce crop yield or even create toxic reactions to plants. |  | N/A | N/A | N/A | #DIV/0! | #DIV/0! |  |  |  |  | #DIV/0! | #DIV/0! |  | Reuse of treated effluent for irrigation/recharge of aquifer | Active | N/A |  |  |  | N/A | N/A |  |  |  | N/A | N/A
| Land for sewage sludge spreading | Active | Flooded land may be unavailable for spreading of sewage sludge; Operational disruption until water recedes; Spillover of floating sludge into the environment; environmental contamination |  |  | N/A | N/A | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! |  | #DIV/0! |  | Land for sewage sludge spreading | Active | Possible changes in soil moisture could affect the available time window for sludge spreading. |  | N/A |  | #DIV/0! | #DIV/0! |  |  | N/A | #DIV/0! | #DIV/0! |  | Land for sewage sludge spreading | Active | A rising groundwater table could prevent land-based dewatering of wastewater sludge (i.e., not sufficient depth below ground level to allow excess water to infiltrate). |  |  | N/A | N/A | #DIV/0! | #DIV/0! |  |  |  | N/A | #DIV/0! | #DIV/0! |  | Land for sewage sludge spreading | Active | Unsafe disposal of low quality sludge matter; risk of soil/ groundwater contamination; |  |  |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | #DIV/0!
Interconnections | Energy Supply | Active | Coastal flooding from sea level rise may threaten power grid infrastructure that lies in the path of rising seas causing power shortages or blackouts. |  |  | N/A | N/A | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! |  | #DIV/0! | Interconnections | Energy Supply | Active | N/A |  | N/A | N/A | N/A | N/A |  |  |  | N/A | N/A | Interconnections | Energy Supply | Active | Coastal floods and storm surges (exacerbated by sea-level rise) may threaten power grid infrastructure that lies in the path of rising seas causing power shortages or blackouts. |  |  | N/A | N/A | #DIV/0! | #DIV/0! |  |  |  | N/A | #DIV/0! | #DIV/0! | Interconnections | Energy Supply | Active | N/A |  | N/A | N/A | N/A | N/A |  |  |  | N/A | N/A
| Road Connections | Active | Inundated road segments and road closures; disruption of transport services to/from the facility, supply-chain shortages (in case of prolonged disruptions), stranded personnel. |  |  | N/A | N/A | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! |  | #DIV/0! |  | Road Connections | Active | N/A |  | N/A | N/A | N/A | N/A |  |  |  | N/A | N/A |  | Road Connections | Active | Inundation of transportation links may cut off access to the water treatment plant. |  |  | N/A | N/A | #DIV/0! | #DIV/0! |  |  |  | N/A | #DIV/0! | #DIV/0! |  | Road Connections | Active | N/A |  | N/A | N/A | N/A | N/A |  |  |  | N/A | N/A
Instructions
The scope of this step is to help users assess the sensitivity of the project to flooding, drought, sea-level rise and impaired water conditions. The sensitivity scores the proneness of the project to experience physical damage and operational disruptions either because a project component/process has been hampered or because a service provided by interdependent infrastructure has been interrupted.
COMPONENT/ PROCESS SENSITIVITY
1. Start by selecting the type of facility for which the assessment is performed. The selection will automatically inform the contents of Table 2.1 populating the entries of Column D with components/ processes that are typically encountered in the type of facilty selected.
2. Using the drop-down menu of Colum E choose which of the displayed components/processes are relevant to the project under consideration, considering also the interdepedencies of teh project with broader infrastructure systems (i.e., road and prower networks).
3. Rate the sensitivity of each ‘active’ component/process to heavy precipitation and flooding by answering questions Q2.1 to Q2.4. Fill-in only the non-shaded cells. The sensitivity score of the component, will be displayed automatically under the Column ‘Average Sensitivity Score’.
3. Answer questions Q2.5 to Q2.7 to determine the 'Adaptive Capacity' of the component to heavy precipitaiton and flooding – its ability to diminish the consequences of a potential damage/failure and quickly recover to full operation. A non-zero ‘Adaptive Capacity’ score will automatically reduce the actual sensitivity of the component/process, displayed under the column ‘Final Sensitivity Score’.
4.The Final Sensitivity scores (of each 'Active' component/process will be automatically transferred to Step 3, where it will be combined with the exposure data (of Step 1) for the calculation of the respective Vulnerability Score.
5. Repeat the process for the remaining hazards. Answer questions Q2.8 to Q2.10 to assess the sensitivity of each component to ‘Drought’. Continue with questions Q2.11 to Q2.13 to assess the adaptive capacity of the component to the same hazard. Answer questions Q2.14 to Q2.17' and Q2.18 to Q2.21 to assess the sensitivity and the adpative capcity of the various components to sea-level rise and storm surge, and continue with questions Q2.22 to Q2.26 for assessing the individual sensitivities to impaired water conditions.
6. The final sensitivity scores of all components/ processes (Internal and interdependant), for all hazards considered will be automatically transferred to Step 3 to inform the Preliminary Risk Assessment.
DEFINITION OF SENSITIVITY

## Water-Step 3
Climate-proofing of Water & Wastewater Projects against water-related hazards
STEP 3. ASSESS CLIMATE-INDUCED RISKS
Table 3.1 - Overview of the risk profile of the Project (automatically filled using input from the previous sheets)
|  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
|  | EXTREME PRECIPITATION & FLOODING |  |  |  | DROUGHT |  |  |  | SEA-LEVEL RISE & STORM SURGE |  |  |  | IMPAIRED WATER CONDITIONS
| COMPONENTS/ PROCESSES | Sensitivity Score | Exposure Score | Risk Score | Risk Level | Sensitivity Score | Exposure Score | Risk Score | Risk Level | Sensitivity Score | Exposure Score | Risk Score | Risk Level | Sensitivity Score | Exposure Score | Risk Score | Risk Level
| Only active components/processes appear on the list. To activate/deactivate components go to 'Water-Step 2' | [0 -3] | [0 -3] | [0 -9] | [Low ¦ Medium ¦ High] | [0 -3] | [0 -3] | [0 -9] | [Low ¦ Medium ¦ High] | [0 -3] | [0 -3] | [0 -9] | [Low ¦ Medium ¦ High] | [0 -3] | [0 -3] | [0 -9] | [Low ¦ Medium ¦ High]
|  | (Transferred from Step 2) | (Transfered from Step 1) | Risk = Sensitivity x Exposure |  | (Transferred from Step 2) | (Transfered from Step 1) | Risk = Sensitivity x Exposure |  | (Transferred from Step 2) | (Transfered from Step 1) | Risk = Sensitivity x Exposure |  | (Transferred from Step 2) | (Transfered from Step 1) | Risk = Sensitivity x Exposure
Assets, processes, inputs & outputs | Sewerage networks and pumping stations | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | N/A | 0 | N/A | N/A | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0!
| Wastewater treatment plants and processes | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0!
| Receiving river body | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0!
| Reuse of treated effluent for irrigation/recharge of aquifer | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | N/A | 0 | N/A
| Land for sewage sludge spreading | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0!
Interconnections | Energy Supply | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | N/A | 0 | N/A | N/A | #DIV/0! | 0 | #DIV/0! | #DIV/0! | N/A | 0 | N/A | N/A
| Road Connections | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | N/A | 0 | N/A | N/A | #DIV/0! | 0 | #DIV/0! | #DIV/0! | N/A | 0 | N/A | N/A
[12 empty] | 0 |  |  |  | 0
|  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0!
|  |  |  | #DIV/0! |  |  |  | 0 |  |  |  | #DIV/0! |  |  |  | 0
Instructions
The scope of this step is to help users identify components/ processes/ interconnections that may be negatively affected in the event of flooding, drought, sea-level rise or impaired water conditions.
1. Table 3.1 summarizes the risk profile of the project. The risk of each component is estimated automatically by combining the sensitivity and the exposure scores of the previous Steps. Risks are reported in a dual format: using an arithmetic scale from [0-9] and a qualitative description [Low-Medium-High].
3. The Risk scores are automatically transferred to Step 4, to inform the selection of adaptation measures.
DEFINITION OF RISK

## Water-Step 4
Climate-proofing of Water & Wastewater Projects against water-related hazards
STEP 4. SELECT ADAPTATION MEASURES AND CHECK CLIMATE-PROOFING
|  | Type of Facility: | Wastewater Collection & Treatment
|  | Assets, processes, inputs & outputs |  |  |  |  | Interconnections
Table 4.1 - Climate-proofing checklist
| Components (Only active components appear on the list. To activate/deactivate components go to 'Water-Step 2') | Sewerage networks and pumping stations | Wastewater treatment plants and processes | Receiving river body | Reuse of treated effluent for irrigation/recharge of aquifer | Land for sewage sludge spreading | Energy Supply | Road Connections
Climate proofing against FLOODING, SEA LEVEL RISE & IMPAIRED WATER CONDITIONS
4.1a | Initial Risk Score to HEAVY PRECIPITATION & FLOODING (automatically transferred from Step 3) | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
4.1b | Initial Risk Score to SEA-LEVEL RISE & STORM SURGE (automatically transferred from Step 3) | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
4.1c | Initial Risk Score to IMPAIRED WATER CONDITIONS (automatically transferred from Step 3) | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | N/A | N/A
4.2 | Adaptation Measures for combating FLOODING, SEA-LEVEL RISE & IMPAIRED WATER CONDITIONS
List up to 10 applicable adaptation measures from Tables 4.2 & 4.3
…
…
…
…
…
…
…
…
| … | [11 empty] | Flood
4.3 | Provide an Efficiency Score for the selected measures | High | [10 empty] | High
| Answer [ 'Low' or 'High']. Leave blank if no adaptation measures are foreseen for the particular component. | [9 empty] | High | 0 | 1
4.4a | Final Risk to EXTREME PRECIPITATION & FLOODING | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | Medium | 0
4.4b | Final Risk to SEA-LEVEL RISE & STROM SURGE | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | Low | 0
4.4c | Final Risk to IMPAIRED WATER CONDITIONS | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | N/A | N/A
Sea-Level
| Climate Proofing against DROUGHT | [11 empty] | High
4.5 | Initial Risk Score to DROUGHT (automatically transferred from Step 3) | N/A | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | N/A | N/A |  |  | High | 0 | 1
4.6 | Adaptation Measures for combating DROUGHT | [9 empty] | Medium | 0
| List up to 10 applicable adaptation measures from Tables 4.2 & 4.3 | [9 empty] | Low | 0
Impaired water
| … | [11 empty] | High
| … | [9 empty] | High | 0 | 1
| … | [9 empty] | Medium | 0
| … | [9 empty] | Low | 0
…
…
…
…
…
4.7 | Provide an Efficiency Score for the selected measures |  |  | High | [8 empty] | High
| Answer [ 'Low' or 'High']. Leave blank if no adaptation measures are foreseen for the particular component. | [9 empty] | High | 0 | 1
4.8 | Final Risk to DROUGHT | N/A | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | N/A | N/A | 0 | 0 | Medium | 0
[11 empty] | Low | 0
| Table 4.2. Adaptation measures for : | Wastewater Collection & Treatment
|  | Assets, processes, inputs & outputs |  |  |  |  | Interconnections
| List of indicative adaptation measures | Sewerage networks and pumping stations | Wastewater treatment plants and processes | Receiving river body | Reuse of treated effluent for irrigation/recharge of aquifer | Land for sewage sludge spreading | Energy Supply | Road Connections | COST | LIMITATIONS [YES ¦ NO]
| Flooding and Impaired water conditions | \ | [6 empty] | [Expensive ¦ Inexpensive] | Provide your answer. In case of positive answer specify.
| Apply climate-change adjustments in flood design standards (e.g. design precipitation , design flood etc) | High | High | 0 | 0 | High | 0 | 0 | Inexpensive (if performed during planning stage)
| Apply sediment management in rivers (incl. vegetative methods to control stream bank erosion, riparian road improvements, in-stream restoration) | 0 | 0 | High | 0 | 0 | 0 | 0 | Expensive
| Install auxilliary spillways and flood dissipation devices in reservoirs | 0 | 0 | High | 0 | 0 | 0 | 0 | Expensive
| Appy emergency procedure to top off water storage tanks in advance of flooding | 0 | Low | 0 | 0 | 0 | 0 | 0 | Inexpensive
| Install smart Field Devices measuring pressure, temperature, flow - conditions in real time | Low | Low | Low | Low | 0 | 0 | 0 | Expensive
| Apply controls for primary and secondary water/wastewater treatment | 0 | Low | Low | Low | 0 | 0 | 0 | Inexpensive
| Apply advanced treatment techniques (or pre-treatment) to minimize TTS/BOD: microfiltration, UV, RO, high-rate clarification | 0 | High | High | High | 0 | 0 | 0 | Expensive
| Apply fouling control strategies (osmotic backwashing, enzyme cleaning, zeolites, carbon nanotubes, and graphene) | 0 | Low | 0 | 0 | 0 | 0 | 0 | Inexpensive
| Install flood barriers/ shelters around critical assets | High | High | 0 | 0 | High | 0 | 0 | Expensive
| Bolt down chemical tanks containing hazardous material | 0 | Low | 0 | 0 | 0 | 0 | 0 | Inexpensive
| Install UPS, power conditioning and back-up power generators | High | High | 0 | 0 | 0 | 0 | 0 | Expensive
| Install diesel pump stations to ensure the continuation of operations in case of grid blackout | Low | Low | 0 | 0 | 0 | 0 | 0 | Inexpensive
| Install PRVs (pressure reduction valves) to control the risk of high water pressure (which shorten the usable life of pipes, pumps, and connectors) | Low | Low | 0 | 0 | 0 | 0 | 0 | Inexpensive
| Upgrade/seal manholes for future climate-change flood levels | Low | 0 | 0 | 0 | 0 | 0 | 0 | Inexpensive
| Modify the sizing of the mains and the collection network based upon updated climate change modelling | High | 0 | 0 | 0 | 0 | 0 | 0 | Inexpensive (if performed during planning phase)
| Install vertical drains to mitigate the risk of overflow in case of high tide | High | 0 | 0 | 0 | 0 | 0 | 0 | Expensive
| Install backwater valves | Low | 0 | 0 | 0 | 0 | 0 | 0 | Inexpensive
| Install stream inlet sensors and overflow meters to prevent sewage overflows | Low | 0 | 0 | 0 | 0 | 0 | 0 | Inexpensive
| Apply vegetation on the bank side of the outfall to protect from high velocity discharges | Low | 0 | Low | 0 | 0 | 0 | 0 | Inexpensive
| Use rip rap control in areas of high velocity discharges that are most susceptible to soil erosion | High | 0 | High | 0 | 0 | 0 | 0 | Expensive
Protection against Drought
| Modify design standard to accommodate a wider range of possible flow regimes | High | High | 0 | 0 | 0 | 0 | 0 | Inexpensive (if performed during planning stage)
| Increase the energy efficiency of the treatment plant to allow opetation on back-up power longer during emergencies and to reduce electricity cost during normal operations. | 0 | Low | 0 | 0 | 0 | High | 0 | Inexpensive
| Apply advanced treatment techniques to increase biodegradation | 0 | High | High | High | 0 | 0 | 0 | Expensive
| Apply in in-situ monitoring of total suspended solids (TSS) in sewage pipes | Low | 0 | 0 | 0 | 0 | 0 | 0 | Expensive
| Apply advanced sediment removal techniques from pipes (e.g., ice pigging instead of unidirectional flushing) | High | 0 | 0 | 0 | 0 | 0 | 0 | Expensive
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Table 4.3. Adaptation measures for all facilities and all hazards
| Facility-wide protection with No-Regret Solutions | [7 empty] | [Expensive ¦ Inexpensive] | Provide your answer. In case of positive answer specify.
| Consider future flood risk maps when building water infrastructure | High | High | High | 0 | High | 0 | 0 | Inexpensive (if performed in planning phase)
| Implement contingency planning for loss of access routes and prolonged power shortages | 0 | 0 | 0 | 0 | 0 | High | High | Inexpensive
| Set up an emergency response plan: alert system, shut-down protocols, assignment of responsibities | Low | Low | 0 | 0 | 0 | 0 | 0 | Inexpensive
| Increase energy efficiency to allow longer operation on back-up power during emergencies | Low | Low | 0 | 0 | 0 | High | 0 | Inexpensive
| Invest in on-site renewable energy to minimize dependencies on external grid | High | High | 0 | 0 | 0 | High | 0 | Expensive
| Establish regular inspection and maintenance protocols | Low | Low | 0 | 0 | 0 | 0 | 0 | Inexpensive
| Design the treatment facility in a modular manner with sufficient land available for future changes (such as extra filtration or storage capacity to support re-use of treated water for irrigation purposes) | High | High | High | High | High | 0 | 0 | Inexpensive (if performed in planning phase)
Instructions
This step will inform users about the variety of adaptation measures that can be used to climate-proof water and wastewater projects against flooding. drought, sea-level rise and impaired water conditions.
1. An indicative list of adaptation measures is displayed in Table 4.2. Every adaptation measure is linked with one or more components that will benefit from its implementation. Additionally, the Table provides an indication of the level of protection that can be offered by the adaption measure (characterized as either Low or High) and an indicative cost estimate (Expensive or Inexpensive).
In Table 4.3, 'No Regret Solutions are also specified. The latter refer mainly to operational modifications that can be leveraged for protection against risks stemming from failures of the interconnected infrastructure.
CLIMATE PROOFING FOR Extreme Precipitation, Flooding and Sea-level rise
2. Consult Table 4.2 to assemble a tailored adaptation strategy for the facility that reduces its risk. For ease of reference, the risk of each component is automatically transferred herein from the previous step. Select measures that offer protection to moderate or high risk components. Prioritize measures that: (i) offer higher protection; (ii) can benefit multiple components; and (iii) are cost-efficient. Enter the list of selected measures in the Field 4.2. If necessary, the list may be expanded to include additional adaptation measures selected by the user that are not currently listed in Table 4.2.
3. Before finalizing the decision, determine whether there are specific limitations that prevent their implementation. Write down your response at the last columns of Tables 4.2. Limitations to consider: planning restrictions/regulations, space/time limitations, budget constraints, lack of technical experience etc.
5. For every component at risk, determine the efficiency score (i.e., the level of protection) of the selected adaptation strategy). In case the strategy includes more than one measures, determine an aggregated efficiency score considering complementarities between adaptation measures and project specific features and limitations.
Enter the final efficiency score (selecting between 'Hgh' & 'Low' in the white cells of Section 4.3 of Table 4.1
6. The final risk level to 'Extreme precipitation and Flooding' of the various components will be displayed under the section 4.4a of Table 4.1. Similarly, the final risk level to 'Sea-level rise and Storm surge' s will be displayed under the section 4.4b of Table 4.1.
CLIMATE-PROOFING FOR DROUGHT
7. Repeat the same procedure to perform climate-proofing against Drought. Complete sections 4.6 and 4.7 of Table 4.1 to derive the final risk level of the various componensts.
FINAL CHECK
8. The climate-proofing is considered successful when the residual risks of all components (after the implementation of adaptation measures) and all hazards reach the maximum acceptable level. If not, modify the adaptation strategy accordingly and repeat the assessment.
NOTE ON THE EFFICIENCY SCORE
If more than one adaptation measures apply to a specific component, the following rule of thumb could be used for determining their aggregated efficiency score.
Set Efficiency = ‘HIGH’, if at least one selected adaptation measure offers high protection level
Set Efficiency = ‘HIGH’, if positive interactions exist among the selected adaptation measures (e.g., combination of early warning and monitoring)
Set Efficiency = ‘LOW’, in all other cases
Leave black, if no adapatation measure apply.
NOTE ON THE EFFICIENCY SCORE
If more than one adaptation measures apply to a specific component, the following rule of thumb could be used for determining their aggregated efficiency score.
Set Efficiency = ‘HIGH’, if at least one selected adaptation measure offers high protection level
Set Efficiency = ‘HIGH’, if positive interactions exist among the selected adaptation measures (e.g., combination of early warning and monitoring)
Set Efficiency = ‘LOW’, in all other cases
Leave black, if no adapatation measure apply.

## Temperature-Step 1
Climate-proofing of urban regeneration projetcs against temperature-related threats
STEP 1. RATE EXPOSURE combined with likelihood of occurrence
| Table 1.1. Exposure to extreme heat | [5 empty] | Fill-in the white cells
| Question | Instructions | [0] | [1] | [2] | [3] | Provide a score from [0 to 3]
|  |  | NO | LIKELY | MOST LIKELY | YES
Q1.5 | Does the region experience very high temperatures1 during summer? | Temperatures that are consistently higher than the seasonal average are an indication of climate change-induced warming. Answer: 'YES' if high temperatures are quite regular (i.e., several days a month); 'Most Likely' if high temperatures are recorded at least twice a month; 'Likely' if high temperatures are recorded at least once a month; 'NO' in all other cases. | 0 | 1 | 2 | 3
Q1.6 | Has the number of heatwaves increased over the past years? | A heat wave is a period of unusually hot weather (i.e., typically above 5oC than the historic average)that lasts several days or even weeks. If a region is already witnessing an increasing frequency of heatwaves, it is most likely that it will continue to do so. | 0 | 1 | 2 | 3
Q1.7 | Is the 40oC temperature barrier broken more frequently than in the past? | Episodes of very high temperatures rising above 40oC can be devasting for exposed populations while increasing the risk of wildfires. | 0 | 1 | 2 | 3
Q1.8 | Is the project located in a region that has been classified by the national authority as a fire prone area? If such a classification is not available, provide a score based on the proximity of the project to forest areas. | Even if the project is not directly exposed to flames, it may experience some kind of disruption if the broader system is impacted. Answer 'YES' if the distance from the closest forest is < 3km; 'Most likely' if the distance is between 3 and 6 km; 'Likely' if the distance is between 6 to 15 km; and 'No' if the distance is greater than 15 km. | 0 | 1 | 2 | 3
1 What is considered as high temperature may differ across regions. In general, high temperatures are those that exceed the monthly average by more than 5oC.
[5 empty] | Current extreme heat score: |  | #DIV/0!
[5 empty] | Current extreme heat risk: |  | #DIV/0!
[5 empty] | Current wildfire score: |  | #DIV/0!
[5 empty] | Current wildfire risk: |  | #DIV/0!
| Table 1.2. Exposure to extreme cold and freeze-thaw cycles | [5 empty] | Fill-in the white cells
| Question | Instructions | [0] | [1] | [2] | [3] | [0-3]
|  |  | NO | LIKELY | MOST LIKELY | YES | Provide Score
| Question | Instructions | [0] | [1] | [2] | [3] | Provide a score from [0 to 3]
|  |  | NO | LIKELY | MOST LIKELY | YES
Q1.7 | Has the region experienced cold spells during the past 10 -15 years? Cold spells are dangerous weather events characterized by frigid temperatures (below -5oC) and significant duration (several days). | Answer 'YES' if the if cold spells are regular (several times a year); 'Most likely' if cold spells take place with an annual or biannual frequency; 'Likely' if cold spells are infrequent; and 'No' if the region has never experienced a cold spell over the past 15 years. | 0 | 1 | 2 | 3
Q1.8 | Do temperature readings drop below 0oC? How often on a yearly basis? Note that the number of times the temperature readings cross the freezing threshold is directly associated with the freeze-thaw cycles (FTC) in a region. | FTC occurs when air temperature drops low enough to freeze water, then increases enough for it to thaw again. FTC can cause significant damage to infrastructure assets and may contribute to additional runoff, and erosion. Answer 'YES' if the average number of FTCs per year is > 40, 'Most likely' if 20<FTCs< 4, 'Likely' if 5<FTC<20, 'No' if annual FTCs < 5. | 0 | 1 | 2 | 3
Q1.9 | Has the region experienced heavy snowfalls surpassing historic evidence? | Heavy snowfalls that were infrequent in the past, but are now becoming a norm may indicate an upward trend of persistent extreme cold events. | 0 |  |  | 3
[5 empty] | Current extreme cold score: |  | 0
[5 empty] | Current extreme cold risk: |  | Low
Climate Change Projections
(1) Consult the regional climate projections IPCC Interactive Atlas (https://interactive-atlas.ipcc.ch) to determine how temperature patterns will change due to climate change. (2) Specify a climate-change multiplier [from 0.8 to 1.5] that will be used for the estimation of future exposure levels. Base your response on the trajectory of the change (increasing or decreasing) and the associated confidence level (Low, Medium, High). If the trajectory of change is stable set the climate-change multiplier equal to 1.0. Where available, consult downscaled climate projections to refine your answer
| Question | Instructions | Decreasing trend |  | Increasing trend
| Table 1.3. Climate projections |  | Low Confidence | High Confidence | Low Confidence | High Confidence |  |  | Fill-in the white cells
| Question | Instructions | Decreasing trend |  |  | Increasing trend |  |  | Climate-change multiplier
|  |  | Low Confidence | Medium Confidence | High Confidence | Low Confidence | Medium Confidence | High Confidence
Q1.10 | Is the frequency and intentisity of heat waves expected to increase? Will the region experience more hot days year around? | Obtain the regional projections by IPCC for extreme heat to estimate the climate-change multiplier. | 1 | 0.9 | 0.8 | 1.2 | 1.3 | 1.5
Q1.13 | How will climate-change affect winter temperatures? Will winters get colder and heavier? Will the number of frost days increase? | Obtain the regional projections by IPCC for cold spell and frost to estimate the respective climate-change multiplier. | 1 | 0.9 | 0.8 | 1.2 | 1.3 | 1.5
Q1.14 | Is the frequency of Freeze-Thaw Cycles (FTCs) expected to change? | Obtain the mean annual projections of temperature for the location of the project. Assume an increasing FTC trend if the location is historically characterized as a frigid region and the temperature projections are increasing (i.e., as the region is warming it will be easier to reach the freezing threshold). Assume a decreasing FTC trend in all other cases. |  | 0.9 |  |  | 1.3
[5 empty] | Future extreme heat score: |  | #DIV/0!
Future extreme heat risk:
#DIV/0!
[5 empty] | Future wildfire score: |  | #DIV/0!
[5 empty] | Future wildfire risk: |  | #DIV/0!
Future extreme cold score:
0
[5 empty] | Future extreme cold risk: |  | Low
Instructions
Current Exposure (Considering present climate conditions)
1. Use Tables 1.1 and 1.2 to assess the project exposure to extreme temperatures and wildfires. Determine whether the conditions described in the Tables apply to the project under study, and estimate the respective exposure level (Low, Medium, High).
Future Exposure
2. Look up the regional climate projections of IPCC (https://interactive-atlas.ipcc.ch) and observe how temperature patterns are expected to change in the future.
3.Follow the probe Questions of Table 1.3 to to define a climate-change multiplier for each condition described. Set the multiplier > 1 if the trends are increasing (i.e., the region is expected to experience heavier flooding), and < 1 in case milder climate conditions are expected to materialize. The updated exposure level (representing future climate conditions) will be automatically calculated by multiplying the current exposure with the climate-change multiplier.
4. The maximum exposure score (either current or future) for each hazard will be transferred to Step 3 to inform the Preliminary Risk Assessment.
DEFINITION OF EXPOSURE LEVEL
HOW TO USE THE IPCC INTERACTIVE ATLAS to estimate a climate-change multiplier
1. Follow the link : https://interactive-atlas.ipcc.ch
2. Choose Regional Sythesis 3. At the top left corner of the page, select the tab 'Regions' 4. Go to 'Europe' Section and specify the regional subsystem that applies to the project under consideration. 5. The regional climate projections will be appear on the right. Browse the inofrmation provided, to obtain the future trend of the requested climate stressor.

## Temperature-Step 2
Climate-proofing of Water & Wastewater Projects against temperature-related hazards
STEP 2. RATE SENSITIVITY combining impacts and in-built adaptive capacity
|  |  | Use the drop-down menu to select type of the project: | Wastewater Collection & Treatment
Table 2.1. Component-based sensitivity assessment to temperature-related hazards
| Components Selection |  |  | Sensitivity to extreme heat & chronic temperature changes | [5 empty] | Adaptive Capacity to extreme heat & chronic temperature changes |  |  |  | Extreme Heat Score |  |  | Continue the assessment for extreme cold |  |  | Sensitivity to extreme cold | [5 empty] | Adaptive Capacity to extreme cold |  |  |  | Extreme Cold Score |  |  | Continue the assessment for wildfires |  |  | Sensitivity to wildfires |  |  |  |  | Adaptive Capacity to wildfires |  |  |  | Wildfire score
|  |  | 0 | Provide your score in the white cells | [5 empty] | Provide your score in the white cells | [9 empty] | Provide your score in the white cells | [5 empty] | Provide your score in the white cells | [9 empty] | Provide your score in the white cells |  |  |  |  | Provide your score in the white cells
|  |  |  | Q2.1 | Q2.2 | Q2.3 | Q2.4 |  |  | Q2.5 | Q2.6 | Q2.7 | [7 empty] | Q2.8 | Q2.9 | Q2.10 | Q2.11 |  |  | Q2.12 | Q2.13 | Q2.14 | Q2.15 | [6 empty] | Q2.16 | Q2.17 | Q2.18 |  |  | Q2.19 | Q2.20 | Q2.21 | Q2.22
| Select N/A from the drop-down menu to de-activate components that do not apply to the project under consideration |  |  | Based on past experience, will the component remain functional in an extreme heat event? | Is the component protected from extreme heat through applicable measures (e.g. through aeration) | Can the component operate in case of power failure using on-premises power generation? | Will the output (or the performance) of the component be affected by temperature variations? | Average Sensitivity Score | Component Sensitivity | Have any of the adaptation measures (listed in Table 4.2 of Step 4) been included in the design of the specific component? | Are there redundancies that could reduce impacts in case the component fails? | In case of failure, can the component (or its performed function) be quickly replaced/ (restored)? | Final Sensitivity Score |  | Final Sensitivity Level |  |  |  |  | Based on past experience, will the component remain functional when exposed to very low temperatures? | Is the component protected from icing or freezing? (e.g., insulated pipes, steam blowers) | Can the component operate in case of power failure using on-premises power generation? | Is the component sensitive to temperature variations? | Average Sensitivity Score | Component Sensitivity | Have any of the adaptation measures (listed in Tables 4.2 and 4.3 of Step 4) been included in the design of the specific component? | Can the component adopt to changes in temperatures (e.g. through the use of thermoregulatory devices)? | Are there redundancies that could reduce impacts in case the component fails (e.g., process bypassing)? | In case of failure, can the component (or its performed function) be quickly replaced/ restored? | Final Sensitivity Score | Final Sensitivity Level |  |  |  |  | Based on past experience, will the component/process remain functional in case of a wildfire? | Can the component continue to operate in case of power failure (e.g. using on-premises power generation)? | Is the component or the process output insensitive to fugitive smoke? | Average Sensitivity Score | Component Sensitivity | Have any of the adaptation measures (listed in Table 4.2 of Step 4) been included in the design of the specific component? | How fast can the component/proces recover to full operation? | Are there redundancies that could reduce impacts in case the component/process fails? | In case of failure, can the component (or its performed function) be quickly replaced/ (restored)? | Final Sensitivity Score | Final Sensitivity Level
| COMPONENT | SELECTION | POSSIBLE FAILURE MODES | [0: Yes ¦ 3: No] | [0: Yes ¦ 1: Most Likely ¦ 2: Likely ¦ 3: No] | [0: Yes ¦ 1: Most Likely ¦ 2: Likely ¦ 3: No] | [0: No ¦ 1: Yes, above a 10deg increase (from the optimal range) ¦ 2: Yes, above 5deg increase ¦ 3: Yes, even small temperature variations will impair performance] | [0 - 3] | [Low ¦ Medium ¦ High] | [3: Yes, more than one measure of high efficiency, 2: Yes, at least one measure of high efficiency ¦ 1: Yes, at least one measure of low efficiency¦ 0: No adaptation measures] | [3: Yes ¦ 2: Most Likely ¦ 1: Likely ¦ 0: No ] | [3: Yes ¦ 2: Most Likely ¦ 1: Likely ¦ 0: No ] | [0-3] |  | [Low ¦ Medium ¦ High] |  | COMPONENT | SELECTION | POSSIBLE FAILURE MODES | [0: Yes ¦ 3: No] | [0: Yes ¦ 3: No or Unknown] | [0: Yes ¦ 1: Most Likely ¦ 2: Likely ¦ 3: No] | [0: No ¦ 1: Yes, above a 10deg increase (from the optimal range) ¦ 2: Yes, above 5deg increase ¦ 3: Yes, even small temperature variations will impair performance] | [0 - 3] | [Low ¦ Medium ¦ High] | [3: Yes, more than one measure of high efficiency, 2: Yes, at least one measure of high efficiency ¦ 1: Yes, at least one measure of low efficiency¦ 0: No adaptation measures] | [3: Yes ¦ 2: Most Likely ¦ 1: Likely ¦ 0: No ] | [3: Yes ¦ 2: Most Likely ¦ 1: Likely ¦ 0: No ] | [3: Yes ¦ 2: Most Likely ¦ 1: Likely ¦ 0: No ] | [0-3] | [Low ¦ Medium ¦ High] |  | COMPONENT | SELECTION | POSSIBLE FAILURE MODES | [0: Yes ¦ 3: No] | [0: Yes ¦ 1: Most Likely ¦ 2: Likely ¦ 3: No] | [0: Yes ¦ 1: Most Likely ¦ 2: Likely ¦ 3: No] | [0 - 3] | [Low ¦ Medium ¦ High] | [3: All relevant adaptation measures have been included in the original design, 2: Some adaptation measures ¦ 1: Few adaptation measures ¦ 0: No adaptation meassures] | [0: Damage is permanent ¦ 1: Recovery time : several days ¦ 2: Recovery time: ~1 day ¦ 3: Recovery time < 1 day ] | [3: Yes ¦ 2: Most Likely ¦ 1: Likely ¦ 0: No ] | [3: Yes ¦ 2: Most Likely ¦ 1: Likely ¦ 0: No ] | [0-3] | [Low ¦ Medium ¦ High]
Assets, processes, inputs & outputs | Sewerage networks and pumping stations | Active | Unpleasant odors (as a result of intensified bacterial growth); Higher pumping capacity is required to compensate for low-flow rates. |  |  |  |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! |  | #DIV/0! | Assets, processes, inputs & outputs | Sewerage networks and pumping stations | Active | Higher frequency of freeze/thaw cycles may damage concrete pipes (typically used for sewage mains). |  |  |  |  | #DIV/0! | #DIV/0! |  |  |  |  | #DIV/0! | #DIV/0! | Assets, processes, inputs & outputs | Sewerage networks and pumping stations | Active | N/A |  |  |  | N/A | N/A |  |  |  |  | N/A | N/A
| Wastewater treatment plants and processes | Active | Treatment performance may vary with temperature. During warmer (or extreme temperatures) the bacterial processes are intensified leading to increased odor generation and changes in the effluent characteristics; Some treatment processes may be positively impacted (e.g., higher ambient temperature could reduce the required energy for ‘sludge digestion’). |  |  |  |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! |  | #DIV/0! |  | Wastewater treatment plants and processes | Active | Low temperatures may affect the treatment process in several ways: 1. Poor denitrification in aerated ponds; 2. Freezing of surface aerators (leaving aeration tanks more prone to icing); 3. Decreased bacterial activity resulting in BOD effluent; 4. Slower hydrolysis rate (in anaerobic treatment ) limiting the biodegradability of sludge; 5. Increased cost to maintain mesophilic temperature; |  |  |  |  | #DIV/0! | #DIV/0! |  |  |  |  | #DIV/0! | #DIV/0! |  | Wastewater treatment plants and processes | Active | Risk of severe physical damage of valuable assets (i.e., elevated tanks, buildings, and sensitive equipment) exposed to very high temperatures and direct flame |  |  |  | #DIV/0! | #DIV/0! |  |  |  |  | #DIV/0! | #DIV/0!
| Receiving river body | Active | Elevated water temperatures due to the thermal discharge of sewage could change the richness and community composition of the impacted water eco-system (potentially raising broader biodiversity issues) |  |  |  |  | #DIV/0! | #DIV/0! |  |  | N/A | #DIV/0! |  | #DIV/0! |  | Receiving river body | Active | N/A |  |  |  |  | N/A | N/A |  |  |  | N/A | N/A | N/A |  | Receiving river body | Active | N/A |  |  | N/A | N/A | N/A |  |  |  | N/A | N/A | N/A
| Reuse of treated effluent for irrigation/recharge of aquifer | Active | N/A |  |  |  |  | N/A | N/A |  |  | N/A | N/A |  |  |  | Reuse of treated effluent for irrigation/recharge of aquifer | Active | N/A |  |  |  |  | N/A | N/A |  |  |  | N/A | N/A | N/A |  | Reuse of treated effluent for irrigation/recharge of aquifer | Active | Wildfires may change the land that is suitable for cultivation (i.e, leaving soil stripped of nutrients and exposed land to wind/water erosion) thereby the demand for irrigation. |  |  | N/A | #DIV/0! | #DIV/0! |  |  |  | N/A | #DIV/0! | #DIV/0!
| Land for sewage sludge spreading | Active | Warmer temperatures could genrally accelerate biological reactions leading to increased removal efficiencies while decreasing land requirements for sludge disposal |  |  | N/A |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! |  | #DIV/0! |  | Land for sewage sludge spreading | Active | Icing conditions and very low soil temperatures may curtail the available window for sludge spreading |  |  | N/A |  | #DIV/0! | #DIV/0! |  |  |  |  | #DIV/0! | #DIV/0! |  | Land for sewage sludge spreading | Active | Possible effect on soil conditions and suitability for sludge spreading. |  |  | N/A | #DIV/0! | #DIV/0! |  |  |  |  | #DIV/0! | #DIV/0!
Interconnections | Energy Supply | Active | N/A |  |  | N/A | N/A | N/A | N/A |  |  |  | N/A |  | N/A | Interconnections | Energy Supply | Active | Cold spells may overload the grid network causing power shortages and blackouts, obstructing treatment process; risk of discharge of untreated sewage to rivers. |  |  | N/A | N/A | #DIV/0! | #DIV/0! |  |  |  |  | #DIV/0! | #DIV/0! | Interconnections | Energy Supply | Active | Wildfires can physically damage powerlines and substations leading to power outages and blackouts. Even a temporary loss of energy could create a major disruption to the operation of wastewater facility the sewage system (e.g., discharge o untreated sewage to rivers). |  |  |  | #DIV/0! | #DIV/0! |  |  |  |  | #DIV/0! | #DIV/0!
| Road Connections | Active | N/A |  |  | N/A | N/A | N/A | N/A |  |  |  | N/A |  | N/A |  | Road Connections | Active | Iced or snow-blocked roads disrupting transport services to/from the facility |  |  | N/A | N/A | #DIV/0! | #DIV/0! |  |  |  |  | #DIV/0! | #DIV/0! |  | Road Connections | Active | Halted traffic during wildfires obstructing access to the facility |  |  |  | #DIV/0! | #DIV/0! |  |  |  |  | #DIV/0! | #DIV/0!
Instructions
The scope of this step is to help users assess the sensitivity of the project to extreme temperatures and wildfires. The sensitivity scores the proneness of the project to experience physical damage and operational disruptions either because a project component/process has been hampered or because a service provided by interdependent infrastructure has been interrupted.
COMPONENT/ PROCESS SENSITIVITY
1. The facility selection is automatically transfered herein from the previous assessment. To change your selection use the drop-down menu of Water-Step 2.
2. Using the drop-down menu of Colum E choose which of the displayed components/processes are relevant to the project, considering also the interdepedencies of the project with external infrastructure systems (i.e., road and power networks).
3. Rate the sensitivity of each ‘active’ component/process to extreme heat and chronic temerature changes by answering questions Q2.1 to Q2.4. Fill-in only the non-shaded cells. The sensitivity score of the component, will be displayed automatically under the Column ‘Average Sensitivity Score’.
3. Answer questions Q2.5 to Q2.7 to determine the 'Adaptive Capacity' of the component to extreme heat and chronic temperature changes – its ability to diminish the consequences of a potential damage/failure and quickly recover to full operation. A non-zero ‘Adaptive Capacity’ score will automatically reduce the actual sensitivity of the component/process, displayed under the column ‘Final Sensitivity Score’.
4.The Final Sensitivity scores (of each 'Active' component/process will be automatically transferred to Step 3, where it will be combined with the exposure data (of Step 1) for the calculation of the respective Vulnerability Score.
5. Repeat the process for the remaining hazards. Answer questions Q2.8 to Q2.11 to assess the sensitivity of each component to ‘Extreme Cold’. Continue with questions Q2.12 to Q2.15 to assess the adaptive capacity of the component to the same hazard. Answer questions Q2.16 to Q2.18' and Q2.19 to Q2.22 to assess the sensitivity and the adpative capcity of the various components to wildfires.
6. The final sensitivity scores of all components/ processes (Internal and interdependant), for all hazards considered will be automatically transferred to Step 3 to inform the Preliminary Risk Assessment.
DEFINITION OF SENSITIVITY

## Temperature-Step 3
Climate-proofing of Water & Wastewater Projects against temperature-related hazards
STEP 3. ASSESS CLIMATE-INDUCED RISKS
Table 3.1 - Overview of the risk profile of the Project (automatically filled using input from the previous sheets)
|  | EXTREME HEAT |  |  |  | EXTREME COLD |  |  |  | WILDFIRES
| COMPONENTS/ PROCESSES | Sensitivity Score | Exposure Score | Risk Score | Risk Level | Sensitivity Score | Exposure Score | Risk Score | Risk Level | Sensitivity Score | Exposure Score | Risk Score | Risk Level
| Only active components/processes appear on the list. To activate/deactivate components go to 'Temperature-Step 2' | [0 -3] | [0 -3] | [0 -9] | [Low ¦ Medium ¦ High] | [0 -3] | [0 -3] | [0 -9] | [Low ¦ Medium ¦ High] | [0 -3] | [0 -3] | [0 -9] | [Low ¦ Medium ¦ High]
|  | (Transferred from Step 2) | (Transfered from Step 1) | Risk = Sensitivity x Exposure |  | (Transferred from Step 2) | (Transfered from Step 1) | Risk = Sensitivity x Exposure |  | (Transferred from Step 2) | (Transfered from Step 1) | Risk = Sensitivity x Exposure
Assets, processes, inputs & outputs | Sewerage networks and pumping stations | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | N/A | #DIV/0! | N/A | N/A
| Wastewater treatment plants and processes | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Receiving river body | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | N/A | 0 | N/A | N/A | N/A | #DIV/0! | N/A | N/A
| Reuse of treated effluent for irrigation/recharge of aquifer | N/A | #DIV/0! | N/A | N/A | N/A | 0 | N/A | N/A | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Land for sewage sludge spreading | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Interconnections | Energy Supply | N/A | #DIV/0! | N/A | N/A | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Road Connections | N/A | #DIV/0! | N/A | N/A | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | 0 |  |  |  | 0
|  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0!
|  |  |  | 0 |  |  |  | #DIV/0! |  |  |  | #DIV/0!
Instructions
The scope of this step is to help users identify components/ processes/ interconnections that may be negatively affected by temperature extremea and wildfires.
1. Table 3.1 summarizes the risk profile of the project. The risk of each component is estimated automatically by combining the sensitivity and the exposure scores of the previous Steps. Risks are reported in a dual format: using an arithmetic scale from [0-9] and a qualitative description [Low-Medium-High].
3. The Risk scores are automatically transferred to Step 4, to inform the selection of adaptation measures.
DEFINITION OF RISK

## Temperature-Step 4
Climate-proofing of Water & Wastewater Projects against temperature-related hazards
STEP 4. SELECT ADAPTATION MEASURES AND CHECK CLIMATE-PROOFING
|  | Type of Facility: | Wastewater Collection & Treatment
|  | Assets, processes, inputs & outputs |  |  |  |  | Interconnections
Table 4.1 - Climate-proofing checklist
| Components (Only active components appear on the list. To activate/deactivate components go to 'Temperature-Step 2') | Sewerage networks and pumping stations | Wastewater treatment plants and processes | Receiving river body | Reuse of treated effluent for irrigation/recharge of aquifer | Land for sewage sludge spreading | Energy Supply | Road Connections
Climate proofing against HEAVY PRECIPITATION & FLOODING
4.1 | Initial Risk Score to EXTREME HEAT (automatically transferred from Step 3) | #DIV/0! | #DIV/0! | #DIV/0! | N/A | #DIV/0! | N/A | N/A |  |  | High
4.2 | Adaptation Measures for combating EXTREME HEAT
List up to 10 applicable adaptation measures from Tables 4.2 & 4.3
…
…
…
…
…
…
…
…
…
| … | [7 empty] | NOTE
4.3 | Provide an Efficiency Score for the selected measures | [11 empty] | High
| Answer [ 'Low' or 'High']. Leave blank if no adaptation measures are foreseen for the particular component. | [7 empty] | If more than one adaptation measures apply to a specific component, the following rule of thumb could be used for determining their aggregated efficiency score: |  | High | 0 | 1
4.4 | Final Risk to EXTREME HEAT | #DIV/0! | #DIV/0! | #DIV/0! | N/A | #DIV/0! | N/A | N/A | - Set Efficiency = HIGH, if at least one selected adaptation measure offers high protection level |  | Medium | 0
[9 empty] | - Set Efficiency = HIGH, if positive interactions exist among the selected adaptation measures (e.g., combination of early warning and monitoring) |  | Low | 0
| Climate Proofing against EXTREME COLD | [7 empty] | - Set Efficiency = LOW, in all other cases
4.5 | Initial Risk Score to EXTREME COLD (automatically transferred from Step 3) | #DIV/0! | #DIV/0! | N/A | N/A | #DIV/0! | #DIV/0! | #DIV/0!
4.6 | Adaptation Measures for combating EXTREME COLD
List up to 10 applicable adaptation measures from Tables 4.2 & 4.3
…
…
…
…
…
…
…
…
…
…
4.7 | Provide an Efficiency Score for the selected measures
| Answer [ 'Low' or 'High']. Leave blank if no adaptation measures are foreseen for the particular component. | [11 empty] | High
4.8 | Final Risk to EXTREME COLD | #DIV/0! | #DIV/0! | N/A | N/A | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | High | 0 | 1
| Climate Proofing against WILDFIRES | [9 empty] | Medium | 0
4.9 | Initial Risk Score to WILDFIRES (automatically transferred from Step 3) | N/A | #DIV/0! | N/A | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | Low | 0
4.10 | Adaptation Measures for combating WILDFIRES
List up to 10 applicable adaptation measures from Tables 4.2 & 4.3
…
…
…
…
…
…
…
…
…
…
4.11 | Provide an Efficiency Score for the selected measures | [11 empty] | High
| Answer [ 'Low' or 'High']. Leave blank if no adaptation measures are foreseen for the particular component. | [9 empty] | High | 0 | 1
4.12 | Final Risk to WILDFIRES | N/A | #DIV/0! | N/A | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | Medium | 0
[11 empty] | Low | 0
| Table 4.2. Adaptation measures for : | Wastewater Collection & Treatment
|  | Assets, processes, inputs & outputs |  |  |  |  | Interconnections
| List of indicative adaptation measures | Sewerage networks and pumping stations | Wastewater treatment plants and processes | Receiving river body | Reuse of treated effluent for irrigation/recharge of aquifer | Land for sewage sludge spreading | Energy Supply | Road Connections | COST | LIMITATIONS [YES ¦ NO]
| Extreme Heat | [7 empty] | [Expensive ¦ Inexpensive] | Provide your answer. In case of positive answer specify.
| Apply advanced treatment techniques (or pre-treatment) to minimize TTS/BOD: microfiltration, UV, RO, high-rate clarification | 0 | High | High | High | 0 | 0 | 0 | Expensive
| Elevate the concentration of biomass to maintain similar output (e.g. BOD removal) | 0 | High | High | High | 0 | 0 | 0 | Inexpensive
| Apply fouling control strategies (osmotic backwashing, enzyme cleaning, zeolites, carbon nanotubes, and graphene) | 0 | Low | Low | Low | 0 | 0 | 0 | Inexpensive
| Use of thermoregulatory devices to maintain temperatures at optimal levels (e.g. Chiller units) | Low | Low | 0 | 0 | 0 | 0 | 0 | Inexpensive
| Install UPS, power conditioning and back-up power generators | 0 | Low | Low | 0 | 0 | 0 | 0 | Expensive
| Supplement aeration (e.g. by using air compressors with diffusers) | High | High | 0 | 0 | 0 | High | 0 | Inexpensive
| Bypass retention basins in wastewater treatment | Low | Low | 0 | 0 | 0 | 0 | 0 | Inexpensive
| Perform frequent chemical cleaning to remove microrganisms | 0 | Low | 0 | 0 | 0 | 0 | 0 | Inexpensive
| Install diesel pump stations to ensure the continuation of operations in case of grid blackout | Low | Low | 0 | 0 | 0 | 0 | 0 | Expensive
| Apply enhanced odor and corrosion control in wastewater/sewerage systems (e.g., Vapor or fan systems, chemical additions, vapor-phase control technologies etc) | High | High | 0 | 0 | 0 | High | 0 | Expensive
| Identify corrosion and odor hotspots in the sewer network to optimize planning/maintence strategies | High | High | 0 | 0 | 0 | 0 | 0 | Expensive
| 0 | Low | 0 | 0 | 0 | 0 | 0 | 0
Protection against Extreme Cold
| Apply advanced treatment techniques (or pre-treatment) to minimize TTS/BOD: microfiltration, UV, RO, high-rate clarification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Expensive
| Elevate the concentration of biomass to maintain similar output (e.g. BOD removal) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Inexpensive
| Increase nutrients during cooling temperatures | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Expensive
| Increase influent wastewater temperatures by bleeding steam into the sewer system | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Expensive
| Insulation of exposed piping and equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Inexpensive
| Install UPS, power conditioning and back-up power generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Expensive
| Install diesel pump stations to ensure the continuation of operations in case of grid blackout | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Inexpensive
Protection against Wildfires
| Build wildfire barriers around the project | High | High | 0 | 0 | 0 | 0 | High | Expensive
| Install fire-detection monitoring in risk areas | Low | Low | 0 | 0 | Low | 0 | 0 | Expensive
| Prepare evacuation routes in case of a wildfire | 0 | Low | 0 | 0 | 0 | 0 | High | Inexpensive
| Set up a fire suppression system (water tanks, fire sprinklers, emergency firefighting equipment) or enhance the fire-fighting capacity of the facility (e.g., by increasing the water storage capacity). | Low | Low | 0 | 0 | 0 | 0 | 0 | Inexpensive
Table 4.3. Adaptation measures for all facilities and all hazards
| Facility-wide protection with No-Regret Solutions | [7 empty] | [Expensive ¦ Inexpensive] | Provide your answer. In case of positive answer specify.
| Set up an emergency response plan: alert system, shut-down protocols, assignment of responsibities | Low | Low | 0 | 0 | 0 | 0 | 0 | Inexpensive
| Increase energy efficiency to allow longer operation on back-up power during emergencies | Low | Low | 0 | 0 | 0 | High | 0 | Inexpensive
| Invest in n-site renewable energy to minimize dependencies on external grid | 0 | 0 | 0 | 0 | 0 | High | 0 | Inexpensive
| Establish regular inspection and maintenance protocols | Low | Low | Low | Low | Low | 0 | 0 | Inexpensive
| Design the treatment facility in a modular manner with sufficient land available for future changes (such as extra filtration or storage capacity to support re-use of treated water for irrigation purposes) | High | High | High | High | High | 0 | 0 | Inexpensive
Instructions
This step will inform users about the variety of adaptation measures that can be used to climate-proof water and wastewater projects against extreme heat, extreme coald and wildfires.
1. An indicative list of adaptation measures is displayed in Table 4.2.
Every adaptation measure is linked with one or more components that will benefit from its implementation. Additionally, the Table provides an indication of the level of protection that can be offered by the adaption measure (characterized as either Low or High) and an indicative cost estimate (Expensive or Inexpensive).
In Table 4.3, 'No Regret Solutions are also specified. The latter refer mainly to operational modifications that can be leveraged for protection against risks stemming from failures of the interconnected infrastructure.
CLIMATE PROOFING FOR Extreme heat
2. Consult Tables4.2 in order to assemble a tailored adaptation strategy for the project reducing its initial risk below an acceptable level. For ease of reference, the risk of each component/process is automatically transferred herein from the previous step.
3. Select measures that offer protection to moderate or high risk components, and enter your selection in the empty rows of section 4.2. Prioritize measures that: (i) offer higher protection; (ii) can benefit multiple components; and (iii) are cost-efficient. . If necessary, the list may be expanded to include additional adaptation measures selected by the user that are not currently listed in Table 4.2.
4. Before finalizing the decision, determine whether there are specific limitations that prevent their implementation. Write down your response at the last columns of Tables 4.2. Limitations to consider: planning restrictions/regulations, space/time limitations, budget constraints, lack of technical experience etc.
5. For every component at risk, determine the efficiency score (i.e., the level of protection) of the selected adaptation strategy). In case the strategy includes more than one measures, determine an aggregated efficiency score considering complementarities between adaptation measures and project specific features and limitations.
Enter the final efficiency score (selecting between 'Hgh' & 'Low' in the white cells of Section 4.3 of Table 4.1
6. The final risk level to 'EXTREM HEAT' of the various components will be displayed under the section 4.4 of Table 4.1.
CLIMATE-PROOFING FOR EXTREME COLD
7. Repeat the same procedure to perform climate-proofing against Drought. Complete sections 4.6 and 4.7 of Table 4.1 to derive the final risk level of the various componensts/processes.
CLIMATE-PROOFING FOR WILDFIRES
8. Repeat the same procedure to perform climate-proofing against Wildfires. Complete sections 4.10 and 4.11 of Table 4.1 to derive the final risk level of the various componensts/ processes.
FINAL CHECK
8. The climate-proofing is considered successful when the residual risks of all components (after the implementation of adaptation measures) and all hazards reach the maximum acceptable level. If not, modify the adaptation strategy accordingly and repeat the assessment.
NOTE ON THE EFFICIENCY SCORE
If more than one adaptation measures apply to a specific component, the following rule of thumb could be used for determining their aggregated efficiency score.
Set Efficiency = ‘HIGH’, if at least one selected adaptation measure offers high protection level
Set Efficiency = ‘HIGH’, if positive interactions exist among the selected adaptation measures (e.g., combination of early warning and monitoring)
Set Efficiency = ‘LOW’, in all other cases
Leave black, if no adapatation measure apply.
NOTE ON THE EFFICIENCY SCORE
If more than one adaptation measures apply to a specific component, the following rule of thumb could be used for determining their aggregated efficiency score.
Set Efficiency = ‘HIGH’, if at least one selected adaptation measure offers high protection level
Set Efficiency = ‘HIGH’, if positive interactions exist among the selected adaptation measures (e.g., combination of early warning and monitoring)
Set Efficiency = ‘LOW’, in all other cases
Leave black, if no adapatation measure apply.

## Wind-Step 1
Climate-proofing of urban regeneration projects against extreme winds
STEP 1. RATE EXPOSURE combined with likelihood of occurrence
| Table 1.1. Exposure to extreme winds and huricanes | [7 empty] | Fill-in the white cells
| Question | Instructions |  |  | [0] | [1] | [2] | [3] | [0-3]
[5 empty] | NO | LIKELY | MOST LIKELY | YES | Provide Score
Q1.1 | Is the region experiencing disruptive wind events that cause widespread damage (e.g., impassable roads, power outages, unrooted trees, accidents e.t.c)? Are they often? | Extreme Winds are those that exceed 60 knots (> 11 Beaufort). Answer 'Yes' if extreme wind events are happening once a year or more often, 'Most likely' if extreme winds are recurring every 5 years on average; 'Likely' if they do occur but less frequently, and 'No' if the region has never experienced an extreme wind event. |  |  | 0 | 1 | 2 | 3
Q1.2 | Is the facility located at a coastal front? If yes, is the region experiencing exceptionally high waves (surpassing 10 m)? | Considerably stronger winds are typically found in coastal regions compared to sites further inland. Exceptionally high waves in coastal regions are associated with extreme wind conditions. Answer 'Yes' if the facility is at a coastal front and exceptionally high waves are happening once a year or more often, 'Most likely' if exceptionally high waves are recurring every 2-5 years on average; 'Likely' if they do occur but less frequently, and 'No' if the facility is not located in a coastal front. |  |  | 0 | 1 | 2 | 3
Q1.3 | Has the region ever experienced a hurricane? | Although Europe rarely experiences hurricanes, over the past 20 years remnants of hurricanes have reached the coastal regions of Western Europe (Portugal, Ireland, UK etc). As the intensity of hurricanes is projected to increase, the risk of experiencing extreme wind conditions will continue to grow. |  |  | 0 |  |  | 3
[7 empty] | Current extreme wind score: |  | #DIV/0!
[7 empty] | Current extreme wind risk: |  | #DIV/0!
Climate Change Projections
(1) Consult the regional climate projections IPCC Interactive Atlas (https://interactive-atlas.ipcc.ch) to determine how wind-patterns will change due to climate change. (2) Specify a climate-change multiplier [from 0.8 to 1.5] that will be used for the estimation of future exposure levels. Base your response on the trajectory of the change (increasing or decreasing) and the associated confidence level (Low, Medium, High). If the trajectory of change is stable set the climate-change multiplier equal to 1.0. Where available, consult downscaled climate projections to refine your answer.
| Table 1.2. Climate projections | [7 empty] | Fill-in the white cells
| Question | Instructions | Decreasing trend |  |  | Increasing trend |  |  | Climate-change multiplier | `
|  |  | Low Confidence | Medium Confidence | High Confidence | Low Confidence | Medium Confidence | High Confidence
Q1.4 | What is the likelihood of experiencing heavier winds in the future? | Obtain the regional projections by IPCC for extreme wind to estimate the climate-change multiplier. | 1 | 0.9 | 0.8 | 1.2 | 1.3 | 1.5
[7 empty] | Future extreme wind score: |  | #DIV/0!
[7 empty] | Future extreme wind risk: |  | #DIV/0!
Instructions
1. Answer questions Q1.1 to Q1.3 of Table 1.1 to assess the exposure of the facility to extreme wind and hurricanes. Determine whether the conditions described apply to the area of interest and provide the respective score. The exposure score will be automatically calculated .
Future Exposure
2. Look up the regional climate projections of IPCC (https://interactive-atlas.ipcc.ch) and observe how extreme wind sare expected to change in the future.
3. Assign a climate-change multiplier > 1 if extreme wind are expected to intesify and become more frequent or < 1 in the oposite case. The updated exposure levels to ‘extreme wind', ‘will be automatically calculated by combining the current exposure with the climate-change multiplier.
4. The maximum wind exposure score (current or future) will be transferred to Step 3 to inform the Preliminary Risk Assessment.
DEFINITION OF EXPOSURE LEVEL
HOW TO USE THE IPCC INTERACTIVE ATLAS to estimate a climate-change multiplier
1. Follow the link : https://interactive-atlas.ipcc.ch
2. Choose Regional Sythesis 3. At the top left corner of the page, select the tab 'Regions' 4. Go to 'Europe' Section and specify the regional subsystem that applies to the project under consideration. 5. The regional climate projections will be appear on the right. Browse the inofrmation provided, to obtain the future trend of the requested climate stressor.

## Wind-Step 2
Climate-proofing of extreme winds
STEP 2. RATE SENSITIVITY combining impacts and in-built adaptive capacity
|  |  | Use the drop-down menu to select type of the project: | Wastewater Collection & Treatment
Table 2.1. Component-based sensitivity assessment to extreme winds
| Components Selection |  |  | Sensitivity to extreme winds | [5 empty] | Adaptive Capacity to extreme winds |  |  |  |  | Extreme Wind Score
|  |  | 0 | Provide your score in the white cells | [5 empty] | Provide your score in the white cells
|  |  |  | Q2.1 | Q2.2 | Q2.3 | Q2.4 |  |  | Q2.5 | Q2.6 | Q2.7 | Q2.8
| Select N/A from the drop-down menu to de-activate components that do not apply to the project under consideration |  |  | Based on past experience, is the building component expected to remain functional or (sustain minor damage) when exposed to extreme wind gusts? | Is the component designed to withstand increased wind loads? | Is the component wind-protected (e.g., wind-barriers; debris-resistant enclosures for outdoor equipment etc) ? | Is the component and its constituents safely fixed to prevent uplifting or breakage when exposed to extreme gales? | Average Sensitivity Score | Component Sensitivity | Have any of the adaptation measures (listed in Table 4.2 of Step 4) been included in the design of the specific component? | In case of a temporary shutdown, how fast can the component recover to full operation? | In case of failure, can the component (or its performed function) be quickly replaced/ (restored)? | Is there a contingency plan in place to ensure business continuity in case of failure of the intedepedant component? | Final Sensitivity Score |  | Final Sensitivity Level
| COMPONENT | SELECTION | POSSIBLE FAILURE MODES | [0: Yes ¦ 3: No ] | [0: Yes ¦ 3: No] | [0: Yes ¦ 1: Most Likely ¦ 2: Likely ¦ 3: No] | [0: Yes = the fixity connection is strong and has multiple redundancies, 3: No = the fixity connection has a single point of failure] | [0 - 3] | [Low ¦ Medium ¦ High] | [3: Yes, more than one measure of high efficiency, 2: Yes, at least one measure of high efficiency ¦ 1: Yes, at least one measure of low efficiency¦ 0: No adaptation measures] | [3: Recovery time < 1 day ¦ 2: Recovery time: ~1 day ¦ 1: Recovery time : several days ¦ 0: Unrecoverable Damage] | [3: Yes ¦ 2: Most Likely ¦ 1: Likely ¦ 0: No ] | [3: Yes ¦ 0: No] | [0-3] |  | [Low ¦ Medium ¦ High]
Assets, processes, inputs & outputs | Sewerage networks and pumping stations | Active | N/A |  |  |  |  | N/A | N/A |  |  |  | N/A | N/A |  | N/A
| Wastewater treatment plants and processes | Active | N/A |  |  |  |  | N/A | N/A |  |  |  | N/A | N/A |  | N/A
| Receiving river body | Active | N/A |  |  |  |  | N/A | N/A |  |  |  | N/A | N/A |  | N/A
| Reuse of treated effluent for irrigation/recharge of aquifer | N/A | N/A |  |  |  | N/A | N/A | N/A |  | N/A | N/A | N/A | N/A |  | N/A
| Land for sewage sludge spreading | N/A | N/A |  | N/A | N/A | N/A | N/A | N/A |  | N/A | N/A | N/A | N/A |  | N/A
Interconnections | Energy Supply | Active | High winds can snap towers and down power lines causing widespread powerline failure. Even a temporary loss of energy could create a major disruption to the operation of wastewater facility the sewage system (e.g., discharge o untreated sewage to rivers). |  | N/A |  |  | #DIV/0! | #DIV/0! |  |  |  |  | #DIV/0! |  | #DIV/0!
| Road Connections | Active | Blocked roads from fallen objects (e.g. road signage, traffic lights, street lighting, CCTV columns) may temporarily obstruct access to the wastewater facility (for several hours). |  | N/A |  |  | #DIV/0! | #DIV/0! |  |  |  |  | #DIV/0! |  | #DIV/0!
Instructions
The scope of this step is to help users assess the sensitivity of the project to extreme wind conditions and hurricanes. The sensitivity scores the proneness of the project to experience physical damage and operational disruptions either because a project component/process has been hampered or because a service provided by interdependent infrastructure has been interrupted.
COMPONENT/ PROCESS SENSITIVITY
1. The facility selection is automatically transfered herein from the previous assessment. To change your selection use the drop-down menu provided in the Water-Step 2.
2. Using the drop-down menu of Colum E choose which of the displayed components/processes are relevant to the project, considering also the interdepedencies of the project with external infrastructure systems (i.e., road and power networks).
3. Rate the sensitivity of each ‘active’ component/process to extreme heat and chronic temerature changes by answering questions Q2.1 to Q2.4. Fill-in only the non-shaded cells. The sensitivity score of the component, will be displayed automatically under the Column ‘Average Sensitivity Score’.
3. Answer questions Q2.5 to Q2.8 to determine the 'Adaptive Capacity' of the component to extreme wind – its ability to diminish the consequences of a potential damage/failure and quickly recover to full operation. A non-zero ‘Adaptive Capacity’ score will automatically reduce the actual sensitivity of the component/process, displayed under the column ‘Final Sensitivity Score’.
4.The Final Sensitivity scores (of each 'Active' component/process will be automatically transferred to Step 3, where it will be combined with the exposure data (of Step 1) for the calculation of the respective Vulnerability Score.
5. The final sensitivity scores of all components/ processes (Internal and interdependant), for all hazards considered will be automatically transferred to Step 3 to inform the Preliminary Risk Assessment.
DEFINITION OF SENSITIVITY

## Wind-Step 3
Climate-proofing of Water & Wastewater Projects against extreme winds
STEP 3. ASSESS CLIMATE-INDUCED RISKS
Table 3.1 - Overview of the risk profile of the Project (automatically filled using input from the previous sheets)
0
EXTREME WIND
| COMPONENTS/ PROCESSES | Sensitivity Score | Exposure Score | Risk Score | Risk Level
| Only active components/processes appear on the list. To activate/deactivate components go to 'Wind-Step 2' | [0 -3] | [0 -3] | [0 -9] | [Low ¦ Medium ¦ High]
|  | (Transferred from Step 2) | (Transfered from Step 1) | Risk = Sensitivity x Exposure
Assets, processes, inputs & outputs | Sewerage networks and pumping stations | N/A | #DIV/0! | N/A | N/A
| Wastewater treatment plants and processes | N/A | #DIV/0! | N/A | N/A
| Receiving river body | N/A | #DIV/0! | N/A | N/A
|  |  | #DIV/0! | N/A | N/A
|  |  | #DIV/0! | N/A | N/A
Interconnections | Energy Supply | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Road Connections | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
0
#DIV/0!
Instructions
The scope of this step is to help users identify components/ processes/ interconnections that may be negatively affected by extreme winds and hurricanes.
1. Table 3.1 summarizes the risk profile of the project. The risk of each component is estimated automatically by combining the sensitivity and the exposure scores of the previous Steps. Risks are reported in a dual format: using an arithmetic scale from [0-9] and a qualitative description [Low-Medium-High].
3. The Risk scores are automatically transferred to Step 4, to inform the selection of adaptation measures.
DEFINITION OF RISK

## Wind-Step 4
Climate-proofing of Water & Wastewater Projects against extreme winds
STEP 4. SELECT ADAPTATION MEASURES AND CHECK CLIMATE-PROOFING
|  | Type of Facility: | Wastewater Collection & Treatment
|  | Assets, processes, inputs & outputs |  |  |  |  | Interconnections
Table 4.1 - Climate-proofing checklist
| Components (Only active components appear on the list. To activate/deactivate components go to 'Temperature-Step 2') | Sewerage networks and pumping stations | Wastewater treatment plants and processes | Receiving river body | 0 | 0 | Energy Supply | Road Connections
4.1 | Initial Risk Score to EXTREME WIND (automatically transferred from Step 3) | N/A | N/A | N/A | N/A | N/A | #DIV/0! | #DIV/0! |  |  | High
4.2 | Adaptation Measures for combating EXTREME WIND
List up to 10 applicable adaptation measures from Tables 4.2 & 4.3
…
…
…
…
…
…
…
…
…
…
4.3 | Provide an Efficiency Score for the selected measures | [11 empty] | High | 3
| Answer [ 'Low' or 'High']. Leave blank if no adaptation measures are foreseen for the particular component. | [9 empty] | High | 0 | 1
4.4 | Final Risk to EXTREME WIND | N/A | N/A | N/A | N/A | N/A | #DIV/0! | #DIV/0! |  |  | Medium | 0
[11 empty] | Low | 0
[11 empty] | Low | #REF!
| Table 4.2. Adaptation measures for : | Wastewater Collection & Treatment
|  | Assets, processes, inputs & outputs |  |  |  |  | Interconnections
| List of indicative adaptation measures | Sewerage networks and pumping stations | Wastewater treatment plants and processes | Receiving river body | Reuse of treated effluent for irrigation/recharge of aquifer | Land for sewage sludge spreading | Energy Supply | Road Connections | COST | LIMITATIONS [YES ¦ NO]
| Extreme Wind | [7 empty] | [Expensive ¦ Inexpensive] | Provide your answer. In case of positive answer specify.
| Install alert systems for extreme weather events providing warnings ahead of the the impeding storm. | Low | Low | 0 | 0 | 0 | 0 | 0 | Expensive
| Replace elevated tanks with ground-based (where possible). | 0 | High | 0 | 0 | 0 | 0 | 0 | Expensive
| Install wind-proof shelter to protect materials and sensitive equipment from adverse weather conditions | 0 | Low | 0 | 0 | 0 | 0 | 0 | Inexpensive
| Upgrade steel connections using advanced bolting solutions | 0 | Low | 0 | 0 | 0 | 0 | 0 | Inexpensive
| Cover up/Shelter treatment processes to protect containment from flying dust, objects etc. | 0 | Low | 0 | 0 | 0 | 0 | 0 | Inexpensive
| Reinforce lighting protection | Low | 0 | 0 | 0 | 0 | 0 | 0 | Expensive
| Install UPS, power conditioning and back-up power generators | 0 | Low | 0 | 0 | 0 | High | 0 | Expensive
| Install diesel pump stations to ensure the continuation of operations in case of grid blackout | Low | 0 | 0 | 0 | 0 | Low | 0 | Inexpensive
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Table 4.3. Adaptation measures for all facilities and all hazards
| Facility-wide protection with No-Regret Solutions | [7 empty] | [Expensive ¦ Inexpensive] | Provide your answer. In case of positive answer specify.
| Implement contingency planning for loss of access routes and prolonged power shortages | 0 | 0 | 0 | 0 | 0 | 0 | High | Inexpensive
| Set up an emergency response plan: alert system, shut-down protocols, assignment of responsibities | Low | Low | 0 | 0 | 0 | 0 | 0 | Inexpensive
| Increase energy efficiency to allow longer operation on back-up power during emergencies | 0 | 0 | 0 | 0 | 0 | Low | 0 | Inexpensive
| Invest in n-site renewable energy to minimize dependencies on external grid | 0 | 0 | 0 | 0 | 0 | High | 0 | Expensive
| Establish regular inspection and maintenance protocols | Low | Low | Low | Low | Low | 0 | 0 | Inexpensive
| Design the treatment facility in a modular manner with sufficient land available for future changes (such as extra filtration or storage capacity to support re-use of treated water for irrigation purposes) | Low | Low | Low | Low | Low | 0 | 0 | Inexpensive (when performed in planning phase)
Instructions
This step will inform users about the variety of adaptation measures that can be used to climate-proof water and wastewater projects against extreme wind.
1. An indicative list of adaptation measures is displayed in Table 4.2. Each measure may offer a different level of protection ('High' or 'Low') to one or more components/processes and is associated with an indicative cost estimate (Expensive or Inexpensive) displayed under the Column 'COST).
In Table 4.3, 'No Regret Solutions are also specified. The latter refer mainly to operational modifications that can be leveraged for protection against risks stemming from failures of the interconnected infrastructure.
CLIMATE PROOFING FOR Extreme WIND
2. Consult Tables4.2 in order to assemble a tailored adaptation strategy for the project reducing its initial risk below an acceptable level. For ease of reference, the risk of each component/process is automatically transferred herein from the previous step.
3. Select measures that offer protection to moderate or high risk components, and enter your selection in the empty rows of section 4.2. Prioritize measures that: (i) offer higher protection; (ii) can benefit multiple components; and (iii) are cost-efficient. If necessary, the list may be expanded to include additional adaptation measures selected by the user that are not currently listed in Table 4.2.
4. Before finalizing the decision, determine whether there are specific limitations that prevent their implementation. Write down your response at the last columns of Tables 4.2. Limitations to consider: planning restrictions/regulations, space/time limitations, budget constraints, lack of technical experience etc.
5. For every component at risk, determine the efficiency score (i.e., the level of protection) of the selected adaptation strategy). In case the strategy includes more than one measures, determine an aggregated efficiency score considering complementarities between adaptation measures and project specific features and limitations.
Enter the final efficiency score (selecting between 'Hgh' & 'Low' in the white cells of Section 4.3 of Table 4.1
6. The final risk level to 'EXTREME WIND' of the various components will be displayed under the section 4.4 of Table 4.1.
7. The climate-proofing is considered successful when the residual risks of all components (after the implementation of adaptation measures) and all hazards reach the maximum acceptable level. If not, modify the adaptation strategy accordingly and repeat the assessment.
NOTE ON THE EFFICIENCY SCORE
If more than one adaptation measures apply to a specific component, the following rule of thumb could be used for determining their aggregated efficiency score.
Set Efficiency = ‘HIGH’, if at least one selected adaptation measure offers high protection level
Set Efficiency = ‘HIGH’, if positive interactions exist among the selected adaptation measures (e.g., combination of early warning and monitoring)
Set Efficiency = ‘LOW’, in all other cases
Leave black, if no adapatation measure apply.

## Soil-Step 1
Climate-proofing of Water and Waste-water facilities against soil-related hazards
STEP 1. HAZARD EXPOSURE
Table 1.1. Exposure to landslides and soil erosion
Select one option from the drop-down menu.
| How will the assessment be performed? | Empirical Indicators |  |  |  |  | Fill-in the white cells
| Question | Instructions | [0] | [1] | [2] | [3] | Provide a score from [0 to 3]
|  |  | NO | LIKELY | MOST LIKELY | YES
Q1.1 | Is the facility located on a hillside? Is the area characterized by very steep slopes, a lot of loose debris and water, and little vegetation? | Steep hills with low vegetation (or areas that have been recently affected by wildfires) may experience soil erosion, soil creep, rockfalls, and mudslides posing a great threat to assets. [0: No; 1:Yes, on a low-moderate vegetated slope (up to 33% grade); 2: Yes, on a vegetated slope with a moderate to steep grade (33% to 50%) ; 3: Yes, on a steep grade > 50% (with low top soil cover). | 0 | 1 | 2 | 3
Q1.2 | Does the region experience soil movements (i.e., rockfalls, mudslides, soil creep, etc) when it rains? | [0: No; 1: Yes, but rarely; 2: Yes, 3: Yes, frequently] | 0 | 1 | 2 | 3
Q1.3 | Is the region characterized by any of the following: visible gullies; increased tendency of water runoff; poor vegetation growth; decreased thickness of top-soil and exposed plant roots. | [0: No; 3: Yes] | 0 |  |  | 3
1 K-factor [t ha h ha−1 MJ−1 mm−1 is a commonly used indicator that accounts for soil's susceptibility to erosion. Get access to a high-resolution soil erodibility map of Europe here: 10.1016/j.scitotenv.2014.02.010
[5 empty] | Current Landslide Score: |  |  | #DIV/0!
[5 empty] | Current Landslide Risk: |  |  | #DIV/0!
[5 empty] | Current Erosion Score: |  |  | 0
`
[5 empty] | Current Erosion Risk: |  |  | Low
| Table 1.2. Exposure to Saline (Saltwater) Intrusion | [5 empty] | Fill-in the white cells
| Question | Instructions | [0] | [1] | [2] | [3] | Provide a score from [0 to 3]
|  |  | NO | LIKELY | MOST LIKELY | YES
Q1.4 | Is the facility located on a tidal flat? | Low-elevation coastal areas are most vulnerable to sea-water flooding. Seawater from tides and coastal streams flows downwards into the soil leading to the salinization of fresh coastal aquifers. | 0 |  |  | 3
Q1.5 | Coastal regions: Has the irrigation activity of the region increased over the past 15-20 years (e.g. as a result of uncontrolled agricultural development)? | Groundwater over-pumping in coastal regions can draw saltwater into the acquifier reducing fresh water storage capacity. Over- pumping practices are common in agricultural areas with expanded irrigation network. | 0 | 1 | 2 | 3
[5 empty] | Current Saline Intrusion Score: |  | 0
[5 empty] | Current Saline Intrusion Risk: |  | Low
Climate Change Projections
Consult the regional climate projections IPCC Interactive Atlas (https://interactive-atlas.ipcc.ch) to determine how soil-related threats will change due to climate change and specify a climate-change multiplier that will be used for the estimation of future exposure levels. Base your response on the trajectory of the change (increasing or decreasing) and the associated confidence level (Low, Medium, High). If the trajectory of change is stable set the climate-change multiplier equal to 1.0. Where available, consult downscaled climate projections to refine your answer.
Table 1.3. Climate projections
| Question | Instructions | Decreasing trend |  |  | Increasing trend |  |  | Climate-change multiplier
|  |  | Low Confidence | Medium Confidence | High Confidence | Low Confidence | Medium Confidence | High Confidence
Q1.6 | Will the region experience heavier and more frequent coastal storms in the future? Are the trends increasing or decreasing? | Obtain the regional projections by IPCC for coastal flood. Give a score to the climate multiplier by combining information on the direction of change (either decreasing or increasing) and the associated confidence level (Low, Medium, High). | 1 | 0.9 | 0.8 | 1.2 | 1.3 | 1.5
Q1.7 | Will the region experience heavier and more frequent rainfalls that could potentially trigger landslides and soil erosion? | Obtain the regional projections by IPCC for 'heavy precipitation and river flood'. Give a score to the climate multiplier by combining information on the direction of change (either decreasing or increasing) and the associated confidence level (Low, Medium, High). | 1 | 0.9 | 0.8 | 1.2 | 1.3 | 1.5
Q1.8 | Is the region expected to become more arid? | Obtain the regional projections by IPCC for ocean aridity. Give a score to the climate multiplier by combining information on the direction of change (either decreasing or increasing) and the associated confidence level (Low, Medium, High). | 1 | 0.9 | 0.8 | 1.2 | 1.3 | 1.5
[5 empty] | Future Landslide/ Soil Erosion Score: |  | #DIV/0!
[5 empty] | Future Landslide/ Soil Erosion Risk: |  | #DIV/0!
[5 empty] | Future Saltwater Intrusion Score: |  | 0
[5 empty] | Future Saltwater Intrusion Risk: |  | Low
Instructions
This step will help users rate the susceptibility of the project area to landslides and soil subsidence considering present and future climate projections.
CURRENT EXPOSURE
1. Select the type of assessment choosing between the two available options. The assessment can be semi-qualitative using available maps or purely qualitatively using empirical indicators. The selection is a matter of user preference and relies on the type of available data. Inexperienced users are advised to use the ‘empirical indicators’ option.
2.Determine whether the conditions described in Table1.1 apply to the area of interest. Fill-in only the non-shaded cells. The exposure score will automatically appear in the respective highlighted cell.
FUTURE PROJECTION
3. Look up the regional climate projections of IPCC (https://interactive-atlas.ipcc.ch) and observe how rainfall patterns are expected to change in the future.
4. Assign a climate-change multiplier > 1 if rainfall trends are incrasing (potentially trigerring more landslides) or < 1 in the oposite case. The updated exposure levels to ‘landlsides', ‘will be automatically calculated by combining the current exposure with the climate-change multiplier.
5. The maximum landslide exposure score (either current or future) will be transferred to Step 3 to inform the Preliminary Risk Assessment.
DEFINITION OF EXPOSURE LEVEL
HOW TO USE THE IPCC INTERACTIVE ATLAS to estimate a climate-change multiplier
1. Follow the link : https://interactive-atlas.ipcc.ch
2. Choose Regional Sythesis 3. At the top left corner of the page, select the tab 'Regions' 4. Go to 'Europe' Section and specify the regional subsystem that applies to the project under consideration. 5. The regional climate projections will be appear on the right. Browse the inofrmation provided, to obtain the future trend of the requested climate stressor.

## Soil-Step 2
Climate-proofing of Water & Wastewater Projects against soil-related hazards
STEP 2. RATE SENSITIVITY combining impacts and in-built adaptive capacity
|  |  | Use the drop-down menu to select type of the project: | Wastewater Collection & Treatment
Table 2.1. Component-based sensitivity assessment to soil-related hazards
| Components Selection |  |  | Sensitivity to landslides and soil-erosion | [6 empty] | Adaptive Capacity to landslides and soil erosion |  |  |  |  | Landslide Score |  |  | Continue the assessment for salt-water intrusion |  |  | Sensitivity to salt-water intrusion |  |  |  |  | Adaptive Capacity to salt-water intrusion |  |  | Extreme Cold Score
|  |  | 0 | Provide your score in the white cells | [6 empty] | Provide your score in the white cells | [10 empty] | Provide your score in the white cells |  |  |  |  | Provide your score in the white cells
|  |  |  | Q2.1 | Q2.2 | Q2.3 | Q2.4 | Q2.5 |  |  | Q2.6 | Q2.7 | Q2.8 | Q2.9 | [7 empty] | Q2.10 | Q2.11 | Q2.12 |  |  | Q2.13 | Q2.14 | Q2.15
| Select N/A from the drop-down menu to de-activate components that do not apply to the project under consideration |  |  | Based on past experience, will the component remain functional (or sustain minimum damage) if exposed to a landslide action? | Can the component sustain landslide impacts without failing? | What is the vegetation coverage in the project location? | Have landslide prevention measures been considered in the design of the component or at its immediate surrounding (e.g., drainage control, terracing of hill sides) | Is the component (or its immediate surrounding) protected from landslide impacts (e.g., rock butreses, nets) | Average Sensitivity Score | Component Sensitivity | Have any of the adaptation measures (listed in Tables 4.2 & 4.3 of Step 4) been included in the design of the specific component? | Can the lanslide design adopt to changing climate conditions (e.g., by using protection nets of higher strength; gradually increasing vegetation coverage) | Are there redundancies that could reduce impacts in case the component fails? (e.g., bypassing pipelines, pumps) | In case of failure, can the component (or its performed function) be quickly replaced (restored)? | Final Sensitivity Score |  | Final Sensitivity Level |  |  |  |  | Based on past experience, will the component/process continue to operate/be performed if increased salinity is detected? | Can the component early detect the salinity threat (e.g., monitoring or control technologies)? | Does the component contain procedures/mechanisms to alleviate the salinity stress (e.g., pretreatment solutions) ? | Average Sensitivity Score | Component Sensitivity | Have any of the adaptation measures (listed in Tables 4.2 and 4.3 of Step 4) been included in the design of the specific component? | Can the component adapt to varying salinity levels (e.g., by adjusting the usage of chemical)? | Can the salinity-affected component or process be quickly recovered, replaced or bypassed? | Final Sensitivity Score | Final Sensitivity Level
| COMPONENT | SELECTION | POSSIBLE FAILURE MODES | [0: Yes ¦ 3: No] | [0: Yes ¦ 1: Most Likely ¦ 2: Likely ¦ 3: No] | [0: Substantial Vegetation coverage ¦1: Light vegetation coverage ¦ 2: Slopes stabilized with organic mulch (or equivalent material) ¦ 3: No Vegetation] | [0: Yes ¦ 1: Most Likely ¦ 2: Likely ¦ 3: No] | [0: Yes ¦ 1: Most Likely ¦ 2: Likely ¦ 3: No] | [0 - 3] | [Low ¦ Medium ¦ High] | [3: Yes, more than one measure of high efficiency, 2: Yes, at least one measure of high efficiency ¦ 1: Yes, at least one measure of low efficiency¦ 0: No adaptation measures] | [3: Yes ¦ 2: Most Likely ¦ 1: Likely ¦ 0: No ] | [3: Yes ¦ 2: Most Likely ¦ 1: Likely ¦ 0: No ] | [3: Yes ¦ 2: Most Likely ¦ 1: Likely ¦ 0: No ] | [0-3] |  | [Low ¦ Medium ¦ High] |  | COMPONENT | SELECTION | POSSIBLE FAILURE MODES | [0: Yes ¦ 3: No ] | [0: Yes ¦ 1: Most Likely ¦ 2: Likely ¦ 3: No ] | [0: Yes¦ 3:No] | [0 - 3] | [Low ¦ Medium ¦ High] | [3: Yes, more than one measure of high efficiency, 2: Yes, at least one measure of high efficiency ¦ 1: Yes, at least one measure of low efficiency¦ 0: No adaptation measures] | [3: Yes ¦ 2: Most Likely ¦ 1: Likely ¦ 0: No ] | [3: Yes ¦ 2: Most Likely ¦ 1: Likely ¦ 0: No ] | [0-3] | [Low ¦ Medium ¦ High]
Assets, processes, inputs & outputs | Sewerage networks and pumping stations | Active | Cracked /broken sewer pipes and mains, dislocated joints/connectors (manhole inlets; pumping stations); loss of containment and sewage spills in the groundwater; Localized erosion around the outfall structure; costly maintenance. | [5 empty] | #DIV/0! | #DIV/0! |  |  |  |  | #DIV/0! |  | #DIV/0! | Assets, processes, inputs & outputs | Sewerage networks and pumping stations | Active | Corrosion of pipes |  |  |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | #DIV/0!
| Wastewater treatment plants and processes | Active | Structural/Foundation failures of tanks/pipes subjected to soil/debris impacts; Potential high concentration of solids and pollutants in the raw effluent leading to: lower treatment efficiency (i.e., longer retention times, imperfect removal of sediments etc); higher energy consumption; accelerated degradation of membranes/filters; lower-quality sludge waste. | [5 empty] | #DIV/0! | #DIV/0! |  |  |  |  | #DIV/0! |  | #DIV/0! |  | Wastewater treatment plants and processes | Active | Increased salinity of the effluent requiring advanced/expensive treatment; Faster degradation of membranes/filters exposed to saline water; Lower quality sludge waste and sewage effluent |  |  |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | #DIV/0!
| Receiving river body | Active | Soil erosion and sediment washing of river banks at the location of discharge outlets; Sediment deposition affects the receiving water quality, raises biodiversity issues and may permantly change the morphology of the channel. | [5 empty] | #DIV/0! | #DIV/0! |  |  |  |  | #DIV/0! |  | #DIV/0! |  | Receiving river body | Active | Toxic/ low quality sewage effluent into fresh-water reservoirs |  |  |  | #DIV/0! | #DIV/0! |  |  |  | #DIV/0! | #DIV/0!
| Reuse of treated effluent for irrigation/recharge of aquifer | N/A | Potentially lower quality effluent, unsuitable for irrigation |  |  | N/A | N/A | N/A | N/A | N/A |  | N/A |  | N/A | N/A |  | N/A |  | Reuse of treated effluent for irrigation/recharge of aquifer | N/A | High salinity effluent may impact crop production and raise public health risks |  |  |  | N/A | N/A |  |  |  | N/A | N/A
| Land for sewage sludge spreading | N/A | Unavailability of sludge spreading areas covered by landslide material; operational disruptions | [5 empty] | N/A | N/A |  |  |  |  | N/A |  | N/A |  | Land for sewage sludge spreading | N/A | Unsafe disposal of low quality sludge matter; risk of soil/ groundwater contamination; Changes in soil composition may affect land suitability for sludge spreading |  |  |  | N/A | N/A |  |  | N/A | N/A | N/A
Interconnections | Energy Supply | Active | Power transmission towers and overhead lines may be physically damaged (or even collapsed) if impacted by a landslide. Failure of a grid component may generate power supply shortages causing operational disruption to energy-dependent operations of the facility. |  |  |  | N/A |  | #DIV/0! | #DIV/0! |  | N/A |  |  | #DIV/0! |  | #DIV/0! | Interconnections | Energy Supply | Active | Saltwater intrusion into aquifers or surface water supplies reduces the availability of freshwater leading to higher energy prices. |  | N/A | N/A | #DIV/0! | #DIV/0! |  | N/A | N/A | #DIV/0! | #DIV/0!
| Road Connections | Active | Road blockages and damages; access restrictions or access cut-off to the plant; |  |  |  | N/A |  | #DIV/0! | #DIV/0! |  | N/A |  |  | #DIV/0! |  | #DIV/0! |  | Road Connections | Active | Saltwater intrusion may reduce the chemical/mechanical properties of soils, increasing the risk of road failure due to subsidence or erosion. |  | N/A | N/A | #DIV/0! | #DIV/0! |  | N/A | N/A | #DIV/0! | #DIV/0!
#DIV/0!
Instructions
The scope of this step is to help users assess the sensitivity of the project to landlsides, soil erosion and salt-water intrusion. The sensitivity scores the proneness of the project to experience physical damage and operational disruptions either because a project component/process has been hampered or because a service provided by interdependent infrastructure has been interrupted.
COMPONENT/ PROCESS SENSITIVITY
1. The facility selection is automatically transfered herein from the previous assessment. To change your selection use the drop-down menu of Water-Step 2.
2. Using the drop-down menu of Colum E choose which of the displayed components/processes are relevant to the project, considering also the interdepedencies of the project with external infrastructure systems (i.e., road and power networks).
3. Rate the sensitivity of each ‘active’ component/process to landlslides and soil erosion by answering questions Q2.1 to Q2.5. Fill-in only the non-shaded cells. The sensitivity score of the component, will be displayed automatically under the Column ‘Average Sensitivity Score’.
3. Answer questions Q2.6 to Q2.9 to determine the 'Adaptive Capacity' of the component to landslides ans soil erosion – its ability to diminish the consequences of a potential damage/failure and quickly recover to full operation. A non-zero ‘Adaptive Capacity’ score will automatically reduce the actual sensitivity of the component/process, displayed under the column ‘Final Sensitivity Score’.
4.The Final Sensitivity scores (of each 'Active' component/process will be automatically transferred to Step 3, where it will be combined with the exposure data (of Step 1) for the calculation of the respective Vulnerability Score.
5. Repeat the process for the remaining hazard. Answer questions Q2.10 to Q2.12 to assess the sensitivity of each component to ‘Salt Water intrusion'. Continue with questions Q2.13 to Q2.15 to assess the adaptive capacity of the component to the same hazard.
6. The final sensitivity scores of all components/ processes (Internal and interdependant) and all hazards considered will be automatically transferred to Step 3 to inform the Preliminary Risk Assessment.
DEFINITION OF SENSITIVITY

## Soil-Step 3
Climate-proofing of Water & Wastewater Projects against soil-related hazards
STEP 3. ASSESS CLIMATE-INDUCED RISKS
Table 3.1 - Overview of the risk profile of the Project (automatically filled using input from the previous sheets)
|  |  |  | 0 |  |  |  | 0
|  | LANDSLIDES & SOIL EROSION |  |  |  | SALTWATER INTRUSION
| COMPONENTS/ PROCESSES | Sensitivity Score | Exposure Score | Risk Score | Risk Level | Sensitivity Score | Exposure Score | Risk Score | Risk Level
| Only active components/processes appear on the list. To activate/deactivate components go to 'Wind-Step 2' | [0 -3] | [0 -3] | [0 -9] | [Low ¦ Medium ¦ High] | [0 -3] | [0 -3] | [0 -9] | [Low ¦ Medium ¦ High]
|  | (Transferred from Step 2) | (Transfered from Step 1) | Risk = Sensitivity x Exposure |  | (Transferred from Step 2) | (Transfered from Step 1) | Risk = Sensitivity x Exposure
Assets, processes, inputs & outputs | Sewerage networks and pumping stations | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0!
| Wastewater treatment plants and processes | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0!
| Receiving river body | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | N/A | N/A |  | 0 | N/A | N/A
|  |  | #DIV/0! | N/A | N/A |  | 0 | N/A | N/A
Interconnections | Energy Supply | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0!
| Road Connections | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0!
|  |  |  | #DIV/0! |  |  |  | #DIV/0!
|  |  |  | #DIV/0! |  |  |  | #DIV/0!
Instructions
The scope of this step is to help users identify components/ processes/ interconnections that may be negatively affected by landslides, soil erosion and saltwater intrusion.
1. Table 3.1 summarizes the risk profile of the project. The risk of each component is estimated automatically by combining the sensitivity and the exposure scores of the previous Steps. Risks are reported in a dual format: using an arithmetic scale from [0-9] and a qualitative description [Low-Medium-High].
3. The Risk scores are automatically transferred to Step 4, to inform the selection of adaptation measures.
DEFINITION OF RISK

## Soil-Step 4
Climate-proofing of Water & Wastewater Projects against soil-related hazards
STEP 4. SELECT ADAPTATION MEASURES AND CHECK CLIMATE-PROOFING
|  | Type of Facility: | Wastewater Collection & Treatment
|  | Assets, processes, inputs & outputs |  |  |  |  | Interconnections
Table 4.1 - Climate-proofing checklist
| Components (Only active components appear on the list. To activate/deactivate components go to 'Temperature-Step 2') | Sewerage networks and pumping stations | Wastewater treatment plants and processes | Receiving river body | 0 | 0 | Energy Supply | Road Connections
Climate proofing against LANDSLIDES & SOIL EROSION
4.1 | Initial Risk Score to LANDSIDES &SOIL EROSION (automatically transferred from Step 3) | #DIV/0! | #DIV/0! | #DIV/0! | N/A | N/A | #DIV/0! | #DIV/0! |  |  | High
4.2 | Adaptation Measures for combating LANDSIDES &SOIL EROSION
List up to 10 applicable adaptation measures from Tables 4.2 & 4.3
…
…
…
…
…
…
…
…
…
…
4.3 | Provide an Efficiency Score for the selected measures | [11 empty] | High | 3
| Answer [ 'Low' or 'High']. Leave blank if no adaptation measures are foreseen for the particular component. | [9 empty] | High | 0 | 1
4.4 | Final Risk to LANDSIDES &SOIL EROSION | #DIV/0! | #DIV/0! | #DIV/0! | N/A | N/A | #DIV/0! | #DIV/0! |  |  | Medium | 0
[11 empty] | Low | 0
| Climate Proofing against SALTWATER INTRUSION | [9 empty] | Medium | 0
4.5 | Initial Risk Score to SALTWATER INTRUSION (automatically transferred from Step 3) | #DIV/0! | #DIV/0! | #DIV/0! | N/A | N/A | #DIV/0! | #DIV/0! |  |  | Low | 0
4.6 | Adaptation Measures for combating SALTWATER INTRUSION
List up to 10 applicable adaptation measures from Tables 4.2 & 4.3
…
…
…
…
…
…
…
…
…
…
4.7 | Provide an Efficiency Score for the selected measures | [11 empty] | High
| Answer [ 'Low' or 'High']. Leave blank if no adaptation measures are foreseen for the particular component. | [9 empty] | High | 0 | 1
4.8 | Final Risk to SALTWATER INTRUSION | #DIV/0! | #DIV/0! | #DIV/0! | N/A | N/A | #DIV/0! | #DIV/0! | 0 | 0 | Medium | 0
[11 empty] | Low | 0
| Table 4.2. Adaptation measures for : | Wastewater Collection & Treatment
|  | Assets, processes, inputs & outputs |  |  |  |  | Interconnections
| List of indicative adaptation measures | Sewerage networks and pumping stations | Wastewater treatment plants and processes | Receiving river body | Reuse of treated effluent for irrigation/recharge of aquifer | Land for sewage sludge spreading | Energy Supply | Road Connections | COST | LIMITATIONS [YES ¦ NO]
| Landslides & Soil Erosion | [7 empty] | [Expensive ¦ Inexpensive] | Provide your answer. In case of positive answer specify.
| Apply advanced treatment techniques (or pre-treatment): microfiltration, UV, RO, high-rate clarification | 0 | High | High | High | 0 | 0 | 0 | Expensive
| Apply antifouling strategies (osmotic backwashing, enzyme cleaning, zeolites, carbon nanotubes, and graphene) | 0 | High | High | High | 0 | 0 | 0 | Expensive
| Design pipeline mains to withstand large ground deformations (e.g., thicker pipelines, enhanced trenching) | High | 0 | 0 | 0 | 0 | 0 | 0 | Inexpensive (if performed in planning phase)
| Plan bypass routes in the piping system | High | 0 | 0 | 0 | 0 | 0 | 0 | Inexpensive (if performed in planning phase)
| Apply facility-wide stromwater management to mitigate excessive run-off that intensifies soil erosion effects and triggers landlides | 0 | Low | 0 | 0 | Low | 0 | 0 | inexpensive
| Install field monitoring in precarious slopes and issue alerts when there is indication of landliding | 0 | High | 0 | 0 | High | 0 | 0 | Expensive
| Apply stabilization measures in unstables slopes threatening critical facilities | 0 | High | 0 | 0 | High | 0 | 0 | Expensive
| Consider suitable design options for outfalls that minimize soil erosion (e.g., submerged outfall) | High | 0 | High | 0 | 0 | 0 | 0 | Inexpensive
| Apply enhanced erosion protection on the bank side of the outfall (vegetation, riprap etc) | High | 0 | High | 0 | 0 | 0 | 0 | Expensive
| Design mains to withstand large ground deformations (e.g., thicker pipelines, enhanced trenching) | High | 0 | 0 | 0 | 0 | 0 | 0 | Expensive
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Protection against Saltwater Intrusion
| Apply contamination controls for primary and secondary water/wastewater treatment | 0 | High | High | High | 0 | 0 | 0 | Expensive
| Apply advanced treatment techniques (or pre-treatment): microfiltration, UV, RO, high-rate clarification | 0 | High | High | High | 0 | 0 | 0 | Expensive
| Invest in high recovery, energy efficient wastewater desalination to maximize freshwater output for reverse osmosis (RO) while saving energy. | 0 | 0 | High | High | 0 | 0 | 0 | Expensive
| Prioritize solutions that are suitable for treating high-salinity brine and wastewater | 0 | 0 | 0 | High | High | 0 | 0 | Expensive
| Optimize pump performace to pevent or postpone clogging conditions (by iron oxide incrustationsa and sediment deposits). Prioritize special-purpose pumps that are critical to the operation of the facility. | Low | Low | 0 | 0 | 0 | 0 | 0 | Inexpensive
| Apply conventional desalintion techniques for saline wastewaters | 0 | High | High | High | 0 | 0 | 0 | Expensive
| Consider biotreatment alternatives that are environmentally friendly and less expensive | 0 | High | High | High | 0 | 0 | 0 | Expensive
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Table 4.3. Adaptation measures for all facilities and all hazards
| Facility-wide protection with No-Regret Solutions | [7 empty] | [Expensive ¦ Inexpensive] | Provide your answer. In case of positive answer specify.
| Implement contingency planning for loss of access routes and prolonged power shortages | 0 | 0 | 0 | 0 | 0 | 0 | High | Inexpensive
| Set up an emergency response plan: alert system, shut-down protocols, assignment of responsibities | Low | Low | 0 | 0 | 0 | 0 | 0 | Inexpensive
| Increase energy efficiency to allow longer operation on back-up power during emergencies | 0 | 0 | 0 | 0 | 0 | Low | 0 | Inexpensive
| Invest in n-site renewable energy to minimize dependencies on external grid | 0 | 0 | 0 | 0 | 0 | High | 0 | Expensive
| Establish regular inspection and maintenance protocols | Low | Low | Low | Low | Low | 0 | 0 | Inexpensive
| Design the treatment facility in a modular manner with sufficient land available for future changes (such as extra filtration or storage capacity to support re-use of treated water for irrigation purposes) | Low | Low | Low | Low | Low | 0 | 0 | Inexpensive (if performed in planning phase)
Instructions
This step will inform users about the variety of adaptation measures that can be used to climate-proof water and wastewater projects against landslides, soil erosion, and slatwater intrusion (as a result of sea-level rise).
1. An indicative list of adaptation measures is displayed in Table 4.2. Each measure may offer a different level of protection ('High' or 'Low') to one or more components/processes and is associated with an indicative cost estimate (Expensive or Inexpensive) displayed under the Column 'COST).
In Table 4.3, 'No Regret Solutions are also specified. The latter refer mainly to operational modifications that can be leveraged for protection against risks stemming from failures of the interconnected infrastructure.
CLIMATE PROOFING FOR LANDSLIDES & SOIL EROSION
2. Consult Tables4.2 in order to assemble a tailored adaptation strategy for the project reducing its initial risk below an acceptable level. For ease of reference, the risk of each component/process is automatically transferred herein from the previous step.
3. Select measures that offer protection to moderate or high risk components, and enter your selection in the empty rows of section 4.2. Prioritize measures that: (i) offer higher protection; (ii) can benefit multiple components; and (iii) are cost-efficient. If necessary, the list may be expanded to include additional adaptation measures selected by the user that are not currently listed in Table 4.2.
4. Before finalizing the decision, determine whether there are specific limitations that prevent their implementation. Write down your response at the last columns of Tables 4.2. Limitations to consider: planning restrictions/regulations, space/time limitations, budget constraints, lack of technical experience etc.
5. For every component at risk, determine the efficiency score (i.e., the level of protection) of the selected adaptation strategy). In case the strategy includes more than one measures, determine an aggregated efficiency score considering complementarities between adaptation measures and project specific features and limitations.
Enter the final efficiency score (selecting between 'Hgh' & 'Low' in the white cells of Section 4.3 of Table 4.1
6. The final risk level to 'LANDSLIDES & SOIL EROSION' of the various components will be displayed under the section 4.4 of Table 4.1.
CLIMATE PROOFING FOR SALTWATER INTRUSION
7. Repeat the same procedure to perform climate-proofing against Drought. Complete sections 4.6 and 4.7 of Table 4.1 to derive the final risk level of the various componensts/processes.
FINAL CHECK
8. The climate-proofing is considered successful when the residual risks of all components (after the implementation of adaptation measures) and all hazards reach the maximum acceptable level. If not, modify the adaptation strategy accordingly and repeat the assessment.
NOTE ON THE EFFICIENCY SCORE
If more than one adaptation measures apply to a specific component, the following rule of thumb could be used for determining their aggregated efficiency score.
Set Efficiency = ‘HIGH’, if at least one selected adaptation measure offers high protection level
Set Efficiency = ‘HIGH’, if positive interactions exist among the selected adaptation measures (e.g., combination of early warning and monitoring)
Set Efficiency = ‘LOW’, in all other cases
Leave black, if no adapatation measure apply.
NOTE ON THE EFFICIENCY SCORE
If more than one adaptation measures apply to a specific component, the following rule of thumb could be used for determining their aggregated efficiency score.
Set Efficiency = ‘HIGH’, if at least one selected adaptation measure offers high protection level
Set Efficiency = ‘HIGH’, if positive interactions exist among the selected adaptation measures (e.g., combination of early warning and monitoring)
Set Efficiency = ‘LOW’, in all other cases
Leave black, if no adapatation measure apply.

## Output
OUTPUT. CLIMATE RISKS BEFORE & AFTER IMPLEMENTATION OF ADAPTATION MEASURES
Before the implementation of adaptation measures
| Heavy Precipitation & Flooding | Drought | Sea-level rise & Storm Surge | Impaired Water Conditions | Extreme Heat | Extreme Cold | Wildfires | Extreme Wind | Landslides & Soil Erosion | Saltwater Intrusion
Initial risk: | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Low | #DIV/0! | #DIV/0!
Maximum risk of interdependencies: | #DIV/0! | Low | #DIV/0! | Low | Low | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
List of high-risk assets/processes: | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
After the implementation of adaptation measures
| Heavy Precipitation & Flooding | Drought | Sea-level rise & Storm Surge | Impaired Water Conditions | Extreme Heat | Extreme Cold | Wildfires | Extreme Wind | Landslides & Soil Erosion | Saltwater Intrusion
Updated risk: | High | High | High | High | High | High | High | High | High | High
Summary of Adaptation Measures (per Hazard)
| Heavy Precipitation & Flooding | Drought | Sea-level rise & Storm Surge | Impaired Water Conditions | Extreme Heat | Extreme Cold | Wildfires | Extreme Wind | Landslides & Soil Erosion | Saltwater Intrusion
1. | 0 | 0 | 0 | 0 | … | … | … | … | … | …
2. | … | … | … |  | … | … | … | … | … | …
3. | … | … | … |  | … | … | … | … | … | …
4. | … | … | … |  | … | … | … | … | … | …
5. | … | … | … |  | … | … | … | … | … | …
6. | … | … | … |  | … | … | … | … | … | …
7. | … | … | … |  | … | … | … | … | … | …
8. | … | … | … |  | … | … | … | … | … | …
9. | … | … | … |  | … | … | … | … | … | …
10. | … | … | … |  | … | … | … | … | … | …
Climate Risk Summary
This is a bird's eye view of the building's climate risk profile before and after the implementation of adaptaiton measures.
Tables are filled in automatically.

## Φύλλο2 (hidden)
| Soil Related |  | Water-related |  |  |  | Temperature-related
| Landslides & Soil Erosion | Saltwater intrusion | Flooding & Seasonal variations | Drought | Impaired Water Quality | Sea Level Rise | Extreme Heat and Changes in Temperature averages | Extreme Cold | Wildfires | Extreme Winds
Drinking Water Supply
Water source | Sediment washing; Abandonment of affected water sources and groundwater wells, Diminished quality of receiving water; Sediment deposition at the intake structure requires frequent dredging to maintain the efficiency of the abstraction and may accelerate bank erosion of downstream areas; Landslide dam breaching causing significant losses in the downstream area (including casualties). | Abandonment of affected water sources and groundwater wells; Diminished quality of receiving water | Reservoir flood discharge affects sediment concentrations at river water intake; Spillway failures (when capacity is exceeded); Increased risk of flooding of the downstream area and threat to human life (e.g.,in case of dam overtopping releasing large amounts of water, sediment, and debris downstream); Seasonal variation in rainfall patterns could alter groundwater aquifer recharge. | Reduced water levels at fresh water reservoirs, decreased water output - difficulty in meeting water demand. | Abandonment of impaired water sources; Reduced water production; Water-supply shortages | Sea-level rise may intensify salt-water intrusion in coastal aquifers hence impacting the availability of water sources. | Increased algal growth in low-flow areas compromising the water quality of the reservoir; Difficulty to meet increased water demands on very hot days; Diminished or more ephemeral snowpacks melting earlier in the season alter groundwater and streamflow dynamics, reducing the available water for use in the warm season; Intensified water scarcity | Salt for road de-icing diluting into the fresh groundwater impairing the water quality of the intake | Wildfires can release heavy metals (e.g., arsenic, mercury), nitrates, and phosphates into water supplies. Rainfall after fires can wash large amounts of sediment, ash, and organic debris into water sources. | N/A
Water distribution network and pumping stations | Sediments drawn into the network decrease pumping efficiency; Pump clogging; Structural breaching of distribution pipes; Damaged/dislocated/broken joints/connectors, Accelerated corrosion of steel pipes (transporting water with high concentration in ions); Foundation failures of tanks (subjected to soil impacts); Sediment buildup in shutoff valves causing malfunctions; Disruption of water service until damage is replaced; | Pump cavitation (as a result of increased water salinity); Increased risk of corrosion-related damages to pipes and tanks | Sediment trapping at the infall structure; Fractured pipes/joints (caused by loss of support, debris impacts); Cracks, leaks, or even the total collapse of tanks exposed to high water levels and debris carried by water; Flood-contaminated water entering the water distribution system through pipe leakage points; Water losses and supply service interruptions. | N/A | Biofilm growth on pipes/tanks, high maintenance cost for flushing/cleaning to avoid bacterial growth | Changes in the groundwater table could be responsible for significant ground deformations impacting the integrity of buried pipelines; Coastal piping systems and their associated components such as pump, shafts, and valves could suffer from severe erosion–corrosion in their metal parts (e.g. valve seats, pump impellers, and pump casings) leading to higher failure rates. | Biofilm growth, significant health risks (if left untreated), more frequent cleaning /flushing of water storage tanks to avoid bacterial growth; Accelerated corrosion rates of pipes/tanks, risk of structural failure of tanks when overloaded; Temperature-induced stressing and cracking of pipes/joints and fitting sections, risk of permeation and leaching (i.e., contaminant entering through the distribution system into the drinking water); Valve sealing failures caused by temperature changes; Increased energy consumption to accommodate higher consumer demand for water during hot days leading to increased operational cost. | Freezing pipes; Ice formation in water storage tanks; Temperature variations may cause extensive cracking of concrete elevated tanks; Temperature-induced stressing and cracking of pipes, risk of permeation and leaching (i.e., contaminant entering through the distribution system into the drinking water); Loss of power (in case of grid blackouts) causing operational disruptions; | Risk of severe physical damage of assets (i.e., tanks, buildings, and equipment) exposed to very high temperatures and direct flame | Possible structural damages of slender and lightweight assets/ componets: elevated tanks, piping racks, suspended frames, hangars,)
Water treatment plant and treatment processes | Imperfect coagulation of the influent; Risk of partial filtering; Lower filter effluent quality; Increased post-treatment needs; Increased waste of backwash water; Accelerated degradation of membranes | Imperfect coagulation of the influent; Risk of partial filtering; Lower filter effluent quality; Increased post-treatment needs; Increased waste of backwash water; Accelerated degradation of membranes | Inundation of treatment tanks; Spill of contaminants/pollutants; Uncontrolled dilution of water influent affecting the efficiency of the treatment process; Filter clogging requiring more frequent replacements; Increased maintenance cost. | Reduced performance of water-cooled chiller units; difficulty in maintaining optimal temperatures, Low quality effluent (high TSS/BOD); Decreased water output (volume). | Advanced water treatment; extended use of chemical additives (during treatment), frequent filter clogging, increased running/maintenance cost | Severe structural damage of coastal plants (damaged tanks, pipes, etc) caused by tidal waves and compound flooding; Risk of permanent shut-down of coastal facilities located across the storm surge zone | Accelerated biofilm growth leading to lower quality (high TSS/BOD) effluent and decreased water production; Rising temperatures tend to reduce the water viscocity (i.e., increasing water flow while decreasing operating pressure) impacting the rate/efficiency of treatment | Temperature drops impact the biochemical reactions (i.e., reaction rates decrease by half for every 10 deg drop in temperature); High BOD effluent; Increased cost to maintain mesophilic temperatures. | Higher sediment loads from burned vegetation, soil, and infrastructure can overwhelm filtration systems, reducing their efficiency. | Possible structural damages of slender and lightweight assets/ componets: elevated tanks, piping racks, suspended frames, hangars,)
| N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Energy Supply | N/A | Saltwater intrusion into aquifers or surface water supplies reduces the availability of freshwater leading to higher energy prices. | Extreme storms and flood events can cause power shortages and blackouts disrupting the operation of the facility in several ways: 1. Inoperable pumps or pump failures; pressure loss; risk of contaminants entering the drinking system, discharge of untreated sewage to rivers; 2. Suspension of key processes (filtration/ purification), sludge build-up in the piping, membrane breakages, failure of diffusers; 3. Electrical failures of critical equipment caused by power surges (during restoration of power outages). | Increased energy cost during prolonged drought periods | The energy sector uses a significant amount of water for extraction, refining, and transport (e.g., for oil and gas). Impaired water conditions increase energy inputs needed to treat or replace water resources. Water shortages can reduce energy availability, stressing the grid and increasing the cost of energy. | Power shortages or blackouts disrupting the operations of the facility in several ways (e.g., pump failures creating loss of pressure in the distribution network) | During heat waves the grid network is overloaded leading to power shortages and blackouts. The operation of the facility may be disrupted in several ways: 1. Inoperable pumps or pump failures; pressure loss; risk of contaminants entering the drinking system, discharge of untreated sewage to rivers; 2. Suspension of key processes (filtration/ purification), sludge build-up in the piping, membrane breakages, failure of diffusers; 3. Electrical failures of critical equipment caused by power surges (during restoration of power outages). | Cold spells may overload the grid network causing power shortages and blackouts. The operation of the facility may be disrupted in several ways: 1. Inoperable pumps or pump failures; pressure loss; risk of contaminants entering the drinking system; 2. Suspension of key processes (filtration/ purification), sludge build-up in the piping, membrane breakages, failure of diffusers; 3. Electrical failures of critical equipment caused by power surges (during restoration of power outages). | Wildfires can physically damage powerlines and substations leading to power outages and blackouts. Even a temporary loss of energy could create a major disruption to the operation of the drinking water utilities causing pressure loss, pump failures, suspension/bypassing of processes with implication on the effluent quality etc). | High winds can snap towers and down power lines causing widespread powerline failure. Even a temporary loss of energy could create a major disruption to the operation of the drinking water utilities causing pressure loss, pump failures, suspension/bypassing of processes with implication on the effluent quality etc).
Road Connections | Landslides can cause severe damage to the road system, in terms of direct (partial or complete destruction of road or blockages) and indirect (access restrictions or access cut-off in case the facility cannot be reached by alternative routes). | Saltwater intrusion may reduce the chemical/mechanical properties of soils, increasing the risk of road failure due to subsidence or erosion. | Inundated road segments and road closures; disruption of transport services to/from the facility, supply-chain shortages (in case of prolonged disruption), stranded personnel. | N/A | N/A | Inundation of transportation links may cut off access to the water treatment plant. | N/A | Iced or snow-blocked roads disrupting transport services to/from the facility | Halted traffic during wildfires obstructing access to the facility | Blocked roads from fallen objects (e.g. road signage, traffic lights, street lighting, CCTV columns) can obstruct access to the water treatment plant (for several hours).
Irrigation
Water from natural water sources | Erosion of the bed and the banks, sediment accumulation into natural water sources; changes in the water quality, more frequent dredging to maintain sufficient water flow. | Abandonment of impacted irrigation wells in case of increased salinity levels; reduced water availability for irrigation; water competition between cities and agriculture (exacerbated during drought periods) | Inlet/pumping blockage (caused by sediment transport into the fresh-water intake) | Reduced water levels at fresh-water reservoirs; Water gap issues (i.e., the fresh-water supply cannot meet the higher demand for irrigation; reduced crop yields if demand can not be met). | Low quality water may impact crop production and raise public health risks | Sea-level rise may intensify salt-water intrusion in coastal aquifers hence impacting the availability of water sources. | Increased algal growth in low-flow areas compromising the water quality of the reservoir | N/A | Wildfires can release heavy metals (e.g., arsenic, mercury), nitrates, and phosphates into water supplies. Rainfall after fires can wash large amounts of sediment, ash, and organic debris into water sources. | N/A
Irrigation network and pumping stations | Collapsed bank soil; Blockage of canals, Fliter/ pump clogging (due to increased sedimentation); | Pump cavitation (as a result of increased water salinity); Higher concentrations of inorganic substances (e.g.salts, sodium ect), can damage the soil and the irrigated crops. | Slope stability issues in dams /canals; flooding of open-channels with contaminated water carrying sediments/pollutants; Leaky pipes and joints, lack of irrigation pressure; Power loss or short circuit damages to electrical components (e.g., power unit, wires,switches) when submerged by flood water. | N/A | Malfunctioning of mechanical equipment; accelerated degradation of pipes and equipment; early system corrosion, pipe blockages. | Changes in the groundwater table could be responsible for significant ground deformations impacting the integrity of buried pipelines; Coastal piping systems and their associated components such as pump, shafts, and valves could suffer from severe erosion–corrosion in their metal parts (e.g. valve seats, pump impellers, and pump casings) leading to higher failure rates. | Water losses in open-air canals as a result of intensified evaporation and vegetation growth; Reduced irrigation efficiency, higher operational cost; Increased irrigation requirements during very hot days | Fractures in the concrete lining of irrigation canals due to soil frost heave,water leakages. | N/A | Possible structural damages of slender and lightweight assets/ components: elevated tanks, piping racks, suspended frames, etc)
| N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Reuse of treated effluent from wastewater treatment plants | Breached/damaged wastewater inlets from landslide actions; low wastewater availability (volume) until the damage replaced | High salinity effluent may impact crop production and raise public health risks | During increased rainfalls (i.e., periods of increased inflow) the effluent quality deteriorates (as a result of decreased detention times in the treatment processes) | Prolonged drought may create ‘high-strength wastewater’ (characterized by higher concentrations in pollutants and pathogens); Low-quality effluent may impact crop production and raise public health risks. | Low-quality effluent (characterized by high concentrations of chemical elements and nutrients) may impact crop production and raise public health risks. | Could significantly alter the land available for irrigation and hence irrigation demand. | Warmer temperatures enhance conversion processes and increase removal efficiencies; Higher effluent quality | Temperature drops negatively impact the wastewater treatment process resulting in lower-quality effluent. | Wildfires may change the land that is suitable for cultivation (i.e, leaving soil stripped of nutrients and exposed land to wind/water erosion) thereby the demand for irrigation. | N/A
| N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Energy Supply | Power transmission towers and overhead lines may be physically damaged (or even collapsed) if impacted by a landslide. Failure of a grid component may generate power supply shortages causing operational disruption to energy-dependent operations of the facility. | Saltwater intrusion into aquifers or surface water supplies reduces the availability of freshwater leading to higher energy prices. | Pumping system shut-down (in case of grid failure); Water cannot be lifted from the source and pressurized to the irrigation system; Sudden pressure losses causing pump failures/malfunctions | N/A | N/A | Coastal floods and storm surges (exacerbated by sea-level rise) may threaten power grid infrastructure that lies in the path of rising seas causing power shortages or blackouts. | Grid network overload, power shortages/ blackouts; Pumping system shut-down; Sudden pressure losses causing pump failures/malfunctions | Grid network overload, power shortages/ blackouts; Pumping system shut-down; Sudden pressure losses causing pump failures/malfunctions | Wildfires can physically damage powerlines and substations. The irrigation facility may experience power outages and blackouts, which apart from the temporary disruption of seervice may also trigger all sorts of electric failures (including pump failures). | High winds can snap towers and down power lines causing widespread powerline failure. The irrigation facility may experience power outages and blackouts, which apart from the temporary disruption of seervice may also trigger all sorts of electric failures (including pump failures).
Road Connections | Road failures/ blockages; Access restrictions or access cut-off | Saltwater intrusion may reduce the chemical/mechanical properties of soils, increasing the risk of road failure due to subsidence or erosion. | Inundated road segments; road closures; obstructed vehicular access to the project premises | N/A | N/A | Inundation of transportation links may cut off access to the water treatment plant. | N/A | Iced or snow-blocked roads obstructing vehicular access to the project premises | Halted traffic during wildfires obstructing access to the facility | Blocked roads from fallen objects (e.g. road signage, traffic lights, street lighting, CCTV columns) may temporarily hinder the accessibility of the irrigation site (for several hours).
Wastewater Collection & Treatment |  |  | Episodic peak flows exceeding the capacity of the sewerage system; Bypassing of treatment; Damaged/cracked mains and laterals caused by uneven settlements; Scouring of riverbanks at discharge outlets; Wastewater backflows into properties.
Sewerage networks and pumping stations | Cracked /broken sewer pipes and mains, dislocated joints/connectors (manhole inlets; pumping stations); loss of containment and sewage spills in the groundwater; Localized erosion around the outfall structure; costly maintenance. | Corrosion of pipes |  | N/A | Faster corrosion of pipes transferring 'high-strength waste-water' (i.e., high in solids and pollutants); Changes in the flow rates and wastewater concentrations could affect the scouring effect and the sedimentation process generating unpleasant odors; Higher pumping capacity may be required to prevent low-flow conditions. | Changes in the groundwater table could be responsible for significant ground deformations impacting the integrity of buried pipelines; Coastal piping systems and their associated components such as pump, shafts, and valves could suffer from severe erosion–corrosion in their metal parts (e.g. valve seats, pump impellers, and pump casings) leading to higher failure rates. | Unpleasant odors (as a result of intensified bacterial growth); Higher pumping capacity is required to compensate for low-flow rates. | Higher frequency of freeze/thaw cycles may damage concrete pipes (typically used for sewage mains). | N/A | N/A
Wastewater treatment plants and processes | Structural/Foundation failures of tanks/pipes subjected to soil/debris impacts; Potential high concentration of solids and pollutants in the raw effluent leading to: lower treatment efficiency (i.e., longer retention times, imperfect removal of sediments etc); higher energy consumption; accelerated degradation of membranes/filters; lower-quality sludge waste. | Increased salinity of the effluent requiring advanced/expensive treatment; Faster degradation of membranes/filters exposed to saline water; Lower quality sludge waste and sewage effluent | `1. Heavy rainfalls could increase the inflow of the Wastewater treatment plants and by extension could decrease the dilution ratio of the infuent. Such a decrease may affect the biological treatment processes and ultimately the quality of the effluent. 2. Flood events can also create severe structural damage to tanks, screens, and all sorts of valuable equipment; 3. During extreme weather, system bypasses can be activated, diverting flows past part or all of the treatment process. | Drought conditions reduce the amount of water that flows into the wastewater treatment; An increased occurrence of low flows could lead to decreased contaminant dilution capacity and higher pollutant concentrations resulting in blockages and early system corrosion. | Low-quality effluent requiring advanced/expensive treatment; Intensified bacterial growth requiring specialized treatment (e.g., extended use of chemical additives; two-staged treatment); Faster degradation/clogging of membranes/filters. | Severe structural damage of coastal plants (damaged tanks, pipes, etc) caused by tidal waves and compound flooding; Significant repair or protection works,(Risk of permanent shut-down or abandonment of stranded assets of located across the storm surge zone. | Treatment performance may vary with temperature. During warmer (or extreme temperatures) the bacterial processes are intensified leading to increased odor generation and changes in the effluent characteristics; Some treatment processes may be positively impacted (e.g., higher ambient temperature could reduce the required energy for ‘sludge digestion’). | Low temperatures may affect the treatment process in several ways: 1. Poor denitrification in aerated ponds; 2. Freezing of surface aerators (leaving aeration tanks more prone to icing); 3. Decreased bacterial activity resulting in BOD effluent; 4. Slower hydrolysis rate (in anaerobic treatment ) limiting the biodegradability of sludge; 5. Increased cost to maintain mesophilic temperature; | Risk of severe physical damage of valuable assets (i.e., elevated tanks, buildings, and sensitive equipment) exposed to very high temperatures and direct flame | N/A
Receiving river body | Soil erosion and sediment washing of river banks at the location of discharge outlets; Sediment deposition affects the receiving water quality, raises biodiversity issues and may permantly change the morphology of the channel. | Toxic/ low quality sewage effluent into fresh-water reservoirs | Episodic peak flows leading to uncontrolled flow of untreated wastewater into receiving water bodies | Low-quality effluent entering fresh water bodies (as a result of reduced dilution at low flow conditions). | Low-quality effluent entering freshwater bodies potentially impairing the water quality below acceptable standards (depending on the assimilative capacity of the watercourse or lake) | Rising receiving-water levels reduce the outflow capacity of the facility; coastal plants may need to change from gravity to pumped effluent thereby increasing energy requirements. | Elevated water temperatures due to the thermal discharge of sewage could change the richness and community composition of the impacted water eco-system (potentially raising broader biodiversity issues) | N/A | N/A | N/A
Reuse of treated effluent for irrigation/recharge of aquifer | Potentially lower quality effluent, unsuitable for irrigation | High salinity effluent may impact crop production and raise public health risks | Seasonal changes in the precipitation pattern may change the demand for irrigation water; an increase in the annual rainfall will lead to higher groundwater levels and will reduce the need fot aquuifer recharging. | Prolonged drought may create ‘high-strength wastewater’ effluent (characterized by higher concentrations in pollutants and pathogens); Risk of health issues if this low-qualaity effluent enters the acquifers or being used for irrigation. | N/A | Could significantly alter the land available for irrigation and hence irrigation demand; Saltwater-intrusion (driven by sea-water rise) may increase the toxicity of effluent beyond allowable standards; unsuitable irrigation water could reduce crop yield or even create toxic reactions to plants. | N/A | N/A | Wildfires may change the land that is suitable for cultivation (i.e, leaving soil stripped of nutrients and exposed land to wind/water erosion) thereby the demand for irrigation. | N/A
Land for sewage sludge spreading | Unavailability of sludge spreading areas covered by landslide material; operational disruptions | Unsafe disposal of low quality sludge matter; risk of soil/ groundwater contamination; Changes in soil composition may affect land suitability for sludge spreading | Flooded land may be unavailable for spreading of sewage sludge; Operational disruption until water recedes; Spillover of floating sludge into the environment; environmental contamination | Possible changes in soil moisture could affect the available time window for sludge spreading. | Unsafe disposal of low quality sludge matter; risk of soil/ groundwater contamination; | A rising groundwater table could prevent land-based dewatering of wastewater sludge (i.e., not sufficient depth below ground level to allow excess water to infiltrate). | Warmer temperatures could genrally accelerate biological reactions leading to increased removal efficiencies while decreasing land requirements for sludge disposal | Icing conditions and very low soil temperatures may curtail the available window for sludge spreading | Possible effect on soil conditions and suitability for sludge spreading. | N/A
Energy Supply | Power transmission towers and overhead lines may be physically damaged (or even collapsed) if impacted by a landslide. Failure of a grid component may generate power supply shortages causing operational disruption to energy-dependent operations of the facility. | Saltwater intrusion into aquifers or surface water supplies reduces the availability of freshwater leading to higher energy prices. | Coastal flooding from sea level rise may threaten power grid infrastructure that lies in the path of rising seas causing power shortages or blackouts. | N/A | N/A | Coastal floods and storm surges (exacerbated by sea-level rise) may threaten power grid infrastructure that lies in the path of rising seas causing power shortages or blackouts. | N/A | Cold spells may overload the grid network causing power shortages and blackouts, obstructing treatment process; risk of discharge of untreated sewage to rivers. | Wildfires can physically damage powerlines and substations leading to power outages and blackouts. Even a temporary loss of energy could create a major disruption to the operation of wastewater facility the sewage system (e.g., discharge o untreated sewage to rivers). | High winds can snap towers and down power lines causing widespread powerline failure. Even a temporary loss of energy could create a major disruption to the operation of wastewater facility the sewage system (e.g., discharge o untreated sewage to rivers).
Road Connections | Road blockages and damages; access restrictions or access cut-off to the plant; | Saltwater intrusion may reduce the chemical/mechanical properties of soils, increasing the risk of road failure due to subsidence or erosion. | Inundated road segments and road closures; disruption of transport services to/from the facility, supply-chain shortages (in case of prolonged disruptions), stranded personnel. | N/A | N/A | Inundation of transportation links may cut off access to the water treatment plant. | N/A | Iced or snow-blocked roads disrupting transport services to/from the facility | Halted traffic during wildfires obstructing access to the facility | Blocked roads from fallen objects (e.g. road signage, traffic lights, street lighting, CCTV columns) may temporarily obstruct access to the wastewater facility (for several hours).

## Φύλλο1 (hidden)
Flood Hazard Maps
Obtain the 50-year, the 100-year, the 200-year flood map for the area of interest. | For areas that are impacted by river floods, experienced users may refer to the 'River Flood Hazard Maps at European and Global Scale' developed by JRC collaborations: https://data.jrc.ec.europa.eu/collection/id-0054
Is the project located within the flood impact zone of the 50-year flood*?
Is the project located within the flood impact zone of the 100-year flood**?
Is the project located within the flood impact zone of the 200-year flood?
Do any of the access routes of the project fall within the flood impact zone of the 100-year flood? | Even if the project remains intact, flooding may hamper accessibility hindering the transit of visiritors to the park and causing supply-chain disruptions.
Flood Risk Maps |  | Landslide Risk Maps & Soil Erodibility Maps
Obtain the flood risk map for the region of interest. Read the color-coded map to determine the exposure level at the area of interest. | If regional flood risk maps are not available, users may refer to the maps developed by the WISE Framewater to identify areas of potential significant flood risk: https://discomap.eea.europa.eu/floodsviewer/ | Based on the landslide susceptibility map, how would you rate the likelihood of a landslide occuring in the area? | [0: No Susceptibility; 1: Low susceptibility; 2: Moderate susceptibility; 3: High susceptibility]. Landslide susceptibility maps measure the potential of a region to experience landslide taking into account historic landslide activity and local conditions (i.e., hill gradient, soil type, water flow in the area).
Is the project located in a high-risk region?* |  | Does the region experience loss of soil cover in erosive rainfall events? | Read the harmonized high-resolution soil erodibility map of Europe and provide a soil erosion score from [0 to 3] based on the reading of the K-factor1. [0: for K-factor between 0 to 0.02; 1 for K-factor between 0.02 to 0.03; 2 for K-factor between 0.03 to 0.04; and 3 for K-factors above 0.04].
Is the project located in a region of moderate risk or higher?**
Is the project located in a region of low risk or higher?
Do any of the access routes of the project fall within the high-risk region? | Even if the project remains intact, flooding may hamper accessibility hindering the transit of visiritors to the park and causing supply-chain disruptions.
Empirical Indicators |  | Empirical Indicators
|  | Is the facility located on a hillside? Is the area characterized by very steep slopes, a lot of loose debris and water, and little vegetation? | Steep hills with low vegetation (or areas that have been recently affected by wildfires) may experience soil erosion, soil creep, rockfalls, and mudslides posing a great threat to assets. [0: No; 1:Yes, on a low-moderate vegetated slope (up to 33% grade); 2: Yes, on a vegetated slope with a moderate to steep grade (33% to 50%) ; 3: Yes, on a steep grade > 50% (with low top soil cover).
Is the project constructed on a floodplain, wetland or a low-lying barrier? | These are flat areas that are close to waterfront (lake or sea). Because of their modest elevation (no more than 10 m) such areas are prone to flooding and storm surges. | Does the region experience soil movements (i.e., rockfalls, mudslides, soil creep, etc) when it rains? | [0: No; 1: Yes, but rarely; 2: Yes, 3: Yes, frequently]
Is the project developed along riverside? | During severe strorms, rivers and streams may overflow covering riverside areas of low elevation. Moreover, high river flows may cause river banks to collapse causing severe damage to riverside developments and infrastructure. | Is the region characterized by any of the following: visible gullies; increased tendency of water runoff; poor vegetation growth; decreased thickness of top-soil and exposed plant roots. | [0: No; 3: Yes]
Has the area experienced significant flooding in recent history? | Answer 'YES' if a major flood event has occurred over the past 50-years; Answer 'NO' if there is no recent memory of a major flood event in the region.
Do any of the access routes of the project fall within a floodplain? | Even if the facility remains intact, flooding may hamper accessibility impacting the supply chain or the transportation of people to/from the project.

## Φύλλο3 (hidden)
Water Facility | Flooding /Impaired Water Quality | Drought | Extreme Heat | Extreme Cold | Wildfires | Landslide/ Soil Erosion | Saltwater intrusion | Extreme Wind
1 | Alternative abstraction sources for emergency periods | Build infrastructure for aquifer storage and recovery (enabling recharge during drought periods) | Apply advanced treatment techniques (or pre-treatment) to minimize TTS/BOD: microfiltration, UV, RO, high-rate clarification | Apply advanced treatment techniques (or pre-treatment) to minimize TTS/BOD: microfiltration, UV, RO, high-rate clarification | Build wildfire barriers around the project | Diversify options for water supply to increase the redundancies of the water facility | Install low-head dams across tidal estuaries to prevent saltwater intrusion | Install alert systems for extreme weather events providing warnings ahead of the the impeding storm.
2 | Apply climate-change adjustments in flood design standards (e.g. design precipitation , design flood etc) | Diversify options for water supply to prevent water scarcity (e.g., Mix surface water and groundwater, employ desalination) | Elevate the concentration of biomass to maintain similar output (e.g. BOD removal) | Elevate the concentration of biomass to maintain similar output (e.g. BOD removal) | Install fire-detection monitoring in risk areas | Apply sediment management practices to control nutrient inputs into source water bodies | Inject fresh water into aquifers or Perform desalination of the abstracted brackish water and recharge the treated water into the aquifer | Replace elevated tanks with ground-based (where possible).
3 | Install flushing structures in the intake to periodically flush out sediments during high flows | Remove sedimentation in reservoirs to increase available water | Apply fouling control strategies (osmotic backwashing, enzyme cleaning, zeolites, carbon nanotubes, and graphene) | Increase nutrients during cooling temepratures | Prepare evacuation routes in case of a wildfire | Preserve or restore vegetated land covers in watersheds to manage stormwater runoff and reduce soil erosion | Reduce and/or rearrange the pattern of boreholes abstraction of groundwater (i.e., use boreholes near the sea during the rainy season and inland boreholes duisng the summer) | Install wind-proof shelter to protect materials and sensitive equipment from adverse weather conditions
4 | Install sluices and fluhing canals to mitigate the transfer of sediments in the intake during high flows | Modify design standards of treatment plants to accommodate a wider range of possible flow regime | Use of thermoregulatory devices to maintain temperatures at optimal levels (e.g. Chiller units) | Insulation of exposed piping and equipment | Set up a fire suppression system (water tanks, fire sprinklers, emergency firefighting equipment) or enhance the fire-fighting capacity of the facility (e.g., by increasing the water storage capacity). | Consider suitable design options for intakes that minimize sendimentation (e.g. bed intake, ubmerged intake) | Apply water contamination monitoring to issue automatic alerts when the quality of the influent is abnormally low | Upgrade steel connections using advanced bolting solutions
5 | Apply sediment management in rivers (incl. vegetative methods to control stream bank erosion, riparian road improvements, in-stream restoration) | Monitor variations in the storage volume of water reservoirs to identify potential need for wider strategic inter-basin water transfers as a back-up supply | Install UPS, power conditioning and back-up power generators | Install UPS, power conditioning and back-up power generators |  | Install flushing structures in the intake to periodically flush out sediments | Apply advanced treatment techniques (or pre-treatment): microfiltration, UV, RO, high-rate clarification | Cover up/Shelter treatment processes to protect containment from flying dust, objects etc.
6 | Install auxilliary spillways and flood dissipation devices in reservoirs | Apply condition monitoring in water pipes to minimize leakages and maximize water consevation | Supplement aeration (e.g. by using air compressors with diffusers) | Install diesel pump stations to ensure the continuation of operations in case of grid blackout |  | Apply water contamination monitoring to issue automatic alerts when the consistency of influent in sediments/ organic matter exceeds maximum thresholds | Apply antifouling strategies (osmotic backwashing, enzyme cleaning, zeolites, carbon nanotubes, and graphene) | Reinforce lighting protection
7 | Appy emergency procedure to top off water storage tanks in advance of flooding | Increase the energy efficiency of the treatment plant to allow opetation on back-up power longer during emergencies and to reduce electricity cost during normal operations. | Perform frequent chemical cleaning to remove microrganisms |  |  | Design pipeline mains to withstand large ground deformations (e.g., thicker pipelines, enhanced trenching) | Optimize pump performace to pevent or postpone clogging conditions. Prioritize special-purpose pumps that are critical to the operation of the facility. | Install UPS, power conditioning and back-up power generators
8 | Install smart Field Devices measuring pressure, temperature, flow - conditions in real time | Establishing water trading (with other utilities) to deal with extreme drought conditions | Install diesel pump stations to ensure the continuation of operations in case of grid blackout |  |  | Plan bypass routes in the piping system |  | Install diesel pump stations to ensure the continuation of operations in case of grid blackout
9 | Apply controls for primary and secondary water treatment | Apply advanced sediment removal techniques from pipes (e.g., ice pigging instead of unidirectional flushing) |  |  |  | Incorporate easy modular extensions to the water supply network (e.g. for future additions of new water sources)
10 | Apply advanced treatment techniques (or pre-treatment) to minimize TTS/BOD: microfiltration, UV, RO, high-rate clarification |  |  |  |  | Optimize pump performace to pevent or postpone clogging conditions (by iron oxide incrustationsa and sediment deposits). Prioritize special-purpose pumps that are critical to the operation of the facility.
11 | Apply fouling control strategies (osmotic backwashing, enzyme cleaning, zeolites, carbon nanotubes, and graphene)
12 | Install flood barriers/ shelters around critical assets
13 | Bolt down chemical tanks containing hazardous material
14 | Install UPS, power conditioning and back-up power generators
15 | Install diesel pump stations to ensure the continuation of operations in case of grid blackout
16 | Install PRVs (pressure reduction valves) to control the risk of high water pressure (which shorten the usable life of pipes, pumps, and connectors)
Wastewater Treatment
1 | Apply climate-change adjustments in flood design standards (e.g. design precipitation , design flood etc) | Modify design standard to accommodate a wider range of possible flow regimes | Apply advanced treatment techniques (or pre-treatment) to minimize TTS/BOD: microfiltration, UV, RO, high-rate clarification | Apply advanced treatment techniques (or pre-treatment) to minimize TTS/BOD: microfiltration, UV, RO, high-rate clarification | Build wildfire barriers around the project | Apply advanced treatment techniques (or pre-treatment): microfiltration, UV, RO, high-rate clarification | Apply contamination controls for primary and secondary water/wastewater treatment | Install alert systems for extreme weather events providing warnings ahead of the the impeding storm.
2 | Apply sediment management in rivers (incl. vegetative methods to control stream bank erosion, riparian road improvements, in-stream restoration) | Increase the energy efficiency of the treatment plant to allow opetation on back-up power longer during emergencies and to reduce electricity cost during normal operations. | Elevate the concentration of biomass to maintain similar output (e.g. BOD removal) | Elevate the concentration of biomass to maintain similar output (e.g. BOD removal) | Install fire-detection monitoring in risk areas | Apply antifouling strategies (osmotic backwashing, enzyme cleaning, zeolites, carbon nanotubes, and graphene) | Apply advanced treatment techniques (or pre-treatment): microfiltration, UV, RO, high-rate clarification | Replace elevated tanks with ground-based (where possible).
3 | Install auxilliary spillways and flood dissipation devices in reservoirs | Apply advanced treatment techniques to increase biodegradation | Apply fouling control strategies (osmotic backwashing, enzyme cleaning, zeolites, carbon nanotubes, and graphene) | Increase nutrients during cooling temperatures | Prepare evacuation routes in case of a wildfire | Design pipeline mains to withstand large ground deformations (e.g., thicker pipelines, enhanced trenching) | Invest in high recovery, energy efficient wastewater desalination to maximize freshwater output for reverse osmosis (RO) while saving energy. | Install wind-proof shelter to protect materials and sensitive equipment from adverse weather conditions
4 | Appy emergency procedure to top off water storage tanks in advance of flooding | Apply in in-situ monitoring of total suspended solids (TSS) in sewage pipes | Use of thermoregulatory devices to maintain temperatures at optimal levels (e.g. Chiller units) | Increase influent wastewater temperatures by bleeding steam into the sewer system | Set up a fire suppression system (water tanks, fire sprinklers, emergency firefighting equipment) or enhance the fire-fighting capacity of the facility (e.g., by increasing the water storage capacity). | Plan bypass routes in the piping system | Prioritize solutions that are suitable for treating high-salinity brine and wastewater | Upgrade steel connections using advanced bolting solutions
5 | Install smart Field Devices measuring pressure, temperature, flow - conditions in real time | Apply advanced sediment removal techniques from pipes (e.g., ice pigging instead of unidirectional flushing) | Install UPS, power conditioning and back-up power generators | Insulation of exposed piping and equipment |  | Apply facility-wide stromwater management to mitigate excessive run-off that intensifies soil erosion effects and triggers landlides | Optimize pump performace to pevent or postpone clogging conditions (by iron oxide incrustationsa and sediment deposits). Prioritize special-purpose pumps that are critical to the operation of the facility. | Cover up/Shelter treatment processes to protect containment from flying dust, objects etc.
6 | Apply controls for primary and secondary water/wastewater treatment |  | Supplement aeration (e.g. by using air compressors with diffusers) | Install UPS, power conditioning and back-up power generators |  | Install field monitoring in precarious slopes and issue alerts when there is indication of landliding | Apply conventional desalintion techniques for saline wastewaters | Reinforce lighting protection
7 | Apply advanced treatment techniques (or pre-treatment) to minimize TTS/BOD: microfiltration, UV, RO, high-rate clarification |  | Bypass retention basins in wastewater treatment | Install diesel pump stations to ensure the continuation of operations in case of grid blackout |  | Apply stabilization measures in unstables slopes threatening critical facilities | Consider biotreatment alternatives that are environmentally friendly and less expensive | Install UPS, power conditioning and back-up power generators
8 | Apply fouling control strategies (osmotic backwashing, enzyme cleaning, zeolites, carbon nanotubes, and graphene) |  | Perform frequent chemical cleaning to remove microrganisms | Install storm/sewer mains below the critical freeze-thaw depth |  | Consider suitable design options for outfalls that minimize soil erosion (e.g., submerged outfall) |  | Install diesel pump stations to ensure the continuation of operations in case of grid blackout
9 | Install flood barriers/ shelters around critical assets |  | Install diesel pump stations to ensure the continuation of operations in case of grid blackout |  |  | Apply enhanced erosion protection on the bank side of the outfall (vegetation, riprap etc)
10 | Bolt down chemical tanks containing hazardous material |  | Apply enhanced odor and corrosion control in wastewater/sewerage systems (e.g., Vapor or fan systems, chemical additions, vapor-phase control technologies etc) |  |  | Design mains to withstand large ground deformations (e.g., thicker pipelines, enhanced trenching)
11 | Install UPS, power conditioning and back-up power generators |  | Identify corrosion and odor hotspots in the sewer network to optimize planning/maintence strategies
12 | Install diesel pump stations to ensure the continuation of operations in case of grid blackout
13 | Install PRVs (pressure reduction valves) to control the risk of high water pressure (which shorten the usable life of pipes, pumps, and connectors)
14 | Upgrade/seal manholes for future climate-change flood levels
15 | Modify the sizing of the mains and the collection network based upon updated climate change modelling
16 | Install vertical drains to mitigate the risk of overflow in case of high tide
17 | Install backwater valves
18 | Install stream inlet sensors and overflow meters to prevent sewage overflows
19 | Apply vegetation on the bank side of the outfall to protect from high velocity discharges
20 | Use rip rap control in areas of high velocity discharges that are most susceptible to soil erosion
21
Irrigation
1 | Alternative abstraction sources for emergency periods | Diversify options for water supply to prevent water scarcity | Use novel materials to suppress algal growth in irrigation canals (e.g. fiberglass reinforced plastic mortar (FRPM) panels ) | Insulation of exposed piping and equipment | Build wildfire barriers around the project | Plan bypass routes in the irrigation system | Reduce and/or rearrange the pattern of boreholes abstraction of groundwater (i.e., use boreholes near the sea during the rainy season and inland boreholes duisng the summer) | Install alert systems for extreme weather events providing warnings ahead of the the impeding storm.
2 | Install UPS, power conditioning and back-up power generators | Apply condition monitoring in water pipes (to minimize leakages and maximize water consevation) |  | Design parabolic canals in seasonally frozen regions to benefit from their excellent hydraulic characteristics and increased frost heave resistance | Install fire-detection monitoring in risk areas | Incorporate easy modular extensions to the supply network (e.g. for future additions of new water sources) | Perform artificial aquifer recharge | Install wind-proof shelter to protect materials and sensitive equipment from adverse weather conditions
3 |  | Replace surface irrigation with drip irrigation systems |  | Apply real-time water flow control to detect leakages and prevent ice build-up/ blockages during very cold days | Prepare evacuation routes in case of a wildfire | Install field monitoring in precarious slopes and issue alerts when there is indication of landliding | Perform soil salinity monitoring | Install UPS, power conditioning and back-up power generators
|  | Plant drought-tolerant crops that demonstrate higher survival rates in arid enviroments |  |  | Set up a fire suppression system (water tanks, fire sprinklers, emergency firefighting equipment) or enhance the fire-fighting capacity of the facility (e.g., by increasing the water storage capacity). | Apply soil erosion measures to unstable slopes | Minimize pumping rates and make batter use of alternative water sources.
|  | Promote rain-harvesting practices and micro-irrigation technologies to limit water agricultural demand |  |  |  |  | Perform regular measurements of the irrigation water quality (i electrical conductivity, Ecw, water sodicity)
Plant high-tolerant crops that can better adopt to saline environements
Replace surface irrigation with drip irrigation systems which are more appropriate for salt sensitive soils.
Optimize irrigation scheduling to eliminate salinity-build-up in the root zone of plants (e.g., Small/frequent intervals for dip irrigation systems, large/less frequent intervals for surface irrigation)
Optimize the design of drainage infrastructure to minimize salts accumulation in root-zone.
Consider a change in the land use if the salinity threat cannot be mitigated

## Water Adaptation (hidden)
Water Facilities-Flooding, Sea-Level rise, Impaired water conditions | [9 empty] | Water Facilities-Drought | [8 empty] | All-Hazards
| Water source | Water distribution network and pumping stations | Water treatment plant and treatment processes |  |  | Energy Supply | Road Connections |  |  | Water source | Water distribution network and pumping stations | Water treatment plant and treatment processes |  |  | Energy Supply | Road Connections |  |  | Water source | Water distribution network and pumping stations | Water treatment plant and treatment processes |  |  | Energy Supply | Road Connections
Alternative abstraction sources for emergency periods | High | [6 empty] | Inexpensive (when performed during planning) | Build infrastructure for aquifer storage and recovery (enabling recharge during drought periods) | High | [6 empty] | Expensive | Consider future flood risk maps when building water infrastructure |  | High | High |  |  |  |  | Inexpensive (if performed in planning phase)
Apply climate-change adjustments in flood design standards (e.g. design precipitation , design flood etc) |  | High | High |  |  |  |  | Inexpensive (when performed during planning) | Diversify options for water supply to prevent water scarcity (e.g., Mix surface water and groundwater, employ desalination) | High | [6 empty] | Expensive | Implement contingency planning for loss of access routes and prolonged power shortages |  | Low | Low |  |  |  | High | Inexpensive
Install flushing structures in the intake to periodically flush out sediments during high flows |  | Low | [5 empty] | Inexpensive | Remove sedimentation in reservoirs to increase available water | High | [6 empty] | Expensive | Set up an emergency response plan: alert system, shut-down protocols, assignment of responsibities |  | High | High |  |  |  |  | Inexpensive
Install sluices and fluhing canals to mitigate the transfer of sediments in the intake during high flows | Low | Low | [5 empty] | Inexpensive | Modify design standards of treatment plants to accommodate a wider range of possible flow regime |  |  | Low |  |  |  |  | Inexpensive (when performed during planning phase) | Increase energy efficiency to allow longer operation on back-up power during emergencies | Low | Low | Low |  |  | High |  | Inexpensive
Apply sediment management in rivers (incl. vegetative methods to control stream bank erosion, riparian road improvements, in-stream restoration) | High | [6 empty] | Expensive | Monitor variations in the storage volume of water reservoirs to identify potential need for wider strategic inter-basin water transfers as a back-up supply | Low |  |  |  |  | High |  | Inexpensive | Invest in on-site renewable energy to minimize dependencies on external grid |  | High | High |  |  | High |  | Expensive
Install auxilliary spillways and flood dissipation devices in reservoirs | High | [6 empty] | Expensive | Apply condition monitoring in water pipes to minimize leakages and maximize water consevation |  | High |  |  |  | Low |  | Expensive | Establish regular inspection and maintenance protocols |  | Low | Low |  |  |  |  | Inexpensive
Appy emergency procedure to top off water storage tanks in advance of flooding |  |  | Low |  |  |  |  | Inexpensive | Increase the energy efficiency of the treatment plant to allow opetation on back-up power longer during emergencies and to reduce electricity cost during normal operations. |  |  | Low |  |  | Low |  | Inexpensive | Design the treatment facility in a modular manner with sufficient land available for future changes (such as extra filtration or storage capacity to support re-use of treated water for irrigation purposes) | Low | Low | Low |  |  |  |  | Inexpensive (if performed in planning phase)
Install smart Field Devices measuring pressure, temperature, flow - conditions in real time |  | Low | Low |  |  |  |  | Expensive | Establishing water trading (with other utilities) to deal with extreme drought conditions | High | [6 empty] | Inexpensive
Apply controls for primary and secondary water treatment |  |  | Low |  |  |  |  | Inexpensive | Apply advanced sediment removal techniques from pipes (e.g., ice pigging instead of unidirectional flushing) |  | High | [5 empty] | Expensive
Apply advanced treatment techniques (or pre-treatment) to minimize TTS/BOD: microfiltration, UV, RO, high-rate clarification |  |  | High |  |  |  |  | Expensive
Apply fouling control strategies (osmotic backwashing, enzyme cleaning, zeolites, carbon nanotubes, and graphene) |  |  | Low |  |  |  |  | Inexpensive
Install flood barriers/ shelters around critical assets |  | High | High |  |  |  |  | Expensive
Bolt down chemical tanks containing hazardous material |  |  | Low |  |  |  |  | Inexpensive
Install UPS, power conditioning and back-up power generators |  | High | High |  |  | High |  | Expensive
Install diesel pump stations to ensure the continuation of operations in case of grid blackout | Low | Low | Low |  |  |  |  | Inexpensive
Install PRVs (pressure reduction valves) to control the risk of high water pressure (which shorten the usable life of pipes, pumps, and connectors) |  | Low | [5 empty] | Inexpensive
Wastewater Treatment -Flooding, Sea-Level rise, Impaired water conditions | [9 empty] | Wastewater Treatment - Drought | [8 empty] | All-Hazards
| Sewerage networks and pumping stations | Wastewater treatment plants and processes | Receiving river body | Reuse of treated effluent for irrigation/recharge of aquifer | Land for sewage sludge spreading | Energy Supply | Road Connections |  |  | Sewerage networks and pumping stations | Wastewater treatment plants and processes | Receiving river body | Reuse of treated effluent for irrigation/recharge of aquifer | Land for sewage sludge spreading | Energy Supply | Road Connections |  |  | Sewerage networks and pumping stations | Wastewater treatment plants and processes | Receiving river body | Reuse of treated effluent for irrigation/recharge of aquifer | Land for sewage sludge spreading | Energy Supply | Road Connections
Apply climate-change adjustments in flood design standards (e.g. design precipitation , design flood etc) | High | High |  |  | High |  |  | Inexpensive (if performed during planning stage) | Modify design standard to accommodate a wider range of possible flow regimes | High | High | [5 empty] | Inexpensive (if performed during planning stage) | Consider future flood risk maps when building water infrastructure | High | High | High |  | High |  |  | Inexpensive (if performed in planning phase)
Apply sediment management in rivers (incl. vegetative methods to control stream bank erosion, riparian road improvements, in-stream restoration) |  |  | High |  |  |  |  | Expensive | Increase the energy efficiency of the traatment palnt to allow opetation on back-up power longer during emergencies and to reduce electricity cost during normal operations. |  | Low |  |  |  | High |  | Inexpensive | Implement contingency planning for loss of access routes and prolonged power shortages | [5 empty] | High | High | Inexpensive
Install auxilliary spillways and flood dissipation devices in reservoirs |  |  | High |  |  |  |  | Expensive | Apply advanced treatment techniques to increase biodegradation |  | High | High | High |  |  |  | Expensive | Set up an emergency response plan: alert system, shut-down protocols, assignment of responsibities | Low | Low | [5 empty] | Inexpensive
Appy emergency procedure to top off water storage tanks in advance of flooding |  | Low | [5 empty] | Inexpensive | Apply in-situ monitoring of total suspended solids (TSS) in sewage pipes | Low | [6 empty] | Expensive | Increase energy efficiency to allow longer operation on back-up power during emergencies | Low | Low |  |  |  | High |  | Inexpensive
Install smart Field Devices measuring pressure, temperature, flow - conditions in real time | Low | Low | Low | Low |  |  |  | Expensive | Apply advanced sediment removal techniques from pipes (e.g., ice pigging instead of unidirectional flushing) | High | [6 empty] | Expensive | Invest in on-site renewable energy to minimize dependencies on external grid | High | High |  |  |  | High |  | Expensive
Apply controls for primary and secondary water/wastewater treatment |  | Low | Low | Low |  |  |  | Inexpensive | [9 empty] | Establish regular inspection and maintenance protocols | Low | Low | [5 empty] | Inexpensive
Apply advanced treatment techniques (or pre-treatment) to minimize TTS/BOD: microfiltration, UV, RO, high-rate clarification |  | High | High | High |  |  |  | Expensive | [9 empty] | Design the treatment facility in a modular manner with sufficient land available for future changes (such as extra filtration or storage capacity to support re-use of treated water for irrigation purposes) | High | High | High | High | High |  |  | Inexpensive (if performed in planning phase)
Apply fouling control strategies (osmotic backwashing, enzyme cleaning, zeolites, carbon nanotubes, and graphene) |  | Low | [5 empty] | Inexpensive
Install flood barriers/ shelters around critical assets | High | High |  |  | High |  |  | Expensive
Bolt down chemical tanks containing hazardous material |  | Low | [5 empty] | Inexpensive
Install UPS, power conditioning and back-up power generators | High | High | [5 empty] | Expensive
Install diesel pump stations to ensure the continuation of operations in case of grid blackout | Low | Low | [5 empty] | Inexpensive
Install PRVs (pressure reduction valves) to control the risk of high water pressure (which shorten the usable life of pipes, pumps, and connectors) | Low | Low | [5 empty] | Inexpensive
Upgrade/seal manholes for future climate-change flood levels | Low | [6 empty] | Inexpensive
Modify the sizing of the mains and the collection network based upon updated climate change modelling | High | [6 empty] | Inexpensive (if performed during planning phase)
Install vertical drains to mitigate the risk of overflow in case of high tide | High | [6 empty] | Expensive
Install backwater valves | Low | [6 empty] | Inexpensive
Install stream inlet sensors and overflow meters to prevent sewage overflows | Low | [6 empty] | Inexpensive
Apply vegetation on the bank side of the outfall to protect from high velocity discharges | Low |  | Low |  |  |  |  | Inexpensive
Use rip rap control in areas of high velocity discharges that are most susceptible to soil erosion | High |  | High |  |  |  |  | Expensive | Irrigation - Drought | [9 empty] | All Hazards
[10 empty] | Water from natural water sources | Irrigation network and pumping stations |  | Reuse of treated effluent from wastewater treatment plants |  | Energy Supply | Road Connections |  |  | Water from natural water sources | Irrigation network and pumping stations |  | Reuse of treated effluent from wastewater treatment plants |  | Energy Supply | Road Connections
| Water from natural water sources | Irrigation network and pumping stations |  | Reuse of treated effluent from wastewater treatment plants |  | Energy Supply | Road Connections |  | Diversify options for water supply to prevent water scarcity | High | [6 empty] | Expensive | Consider future flood risk maps when building water infrastructure |  | High | [5 empty] | Inexpensive (if performed in planning phase)
Alternative abstraction sources for emergency periods | High | [6 empty] | Expensive | Apply condition monitoring in water pipes (to minimize leakages and maximize water consevation) |  | Low | [5 empty] | Expensive | Implement contingency planning for loss of access routes and prolonged power shortages |  | Low |  |  |  |  | High | Inexpensive
Install UPS, power conditioning and back-up power generators |  | High | [5 empty] | Expensive | Replace surface irrigation with drip irrigation systems |  | High | [5 empty] | Inexpensive | Set up an emergency response plan: alert system, shut-down protocols, assignment of responsibities | Low | Low |  | Low |  |  |  | Inexpensive
[9 empty] | Plant drought-tolerant crops that demonstrate higher survival rates in arid enviroments | Low | [6 empty] | Inexpensive | Increase energy efficiency to allow longer operation on back-up power during emergencies |  | Low |  |  |  | High |  | Inexpensive
[9 empty] | Promote rain-harvesting practices and micro-irrigation technologies to limit water agricultural demand | High | [6 empty] | Expensive | Invest in on-site renewable energy to minimize dependencies on external grid |  | High |  |  |  | High |  | Expensive
[18 empty] | Establish regular inspection and maintenance protocols | Low | Low |  | Low |  |  |  | Inexpensive
[18 empty] | Design the treatment facility in a modular manner with sufficient land available for future changes (such as extra filtration or storage capacity to support re-use of treated water for irrigation purposes) | High | High |  | High |  |  |  | Inexpensive (if performed in planning phase)

## Temperature Adaptation (hidden)
Water Facilities-Extreme Heat | [9 empty] | Water Facilities-Extreme Cold | [8 empty] | Water Facilities-Wildfire | [8 empty] | All-Hazards
| Water source | Water distribution network and pumping stations | Water treatment plant and treatment processes |  |  | Energy Supply | Road Connections |  |  | Water source | Water distribution network and pumping stations | Water treatment plant and treatment processes |  |  | Energy Supply | Road Connections |  |  | Water source | Water distribution network and pumping stations | Water treatment plant and treatment processes |  |  | Energy Supply | Road Connections |  |  | Water source | Water distribution network and pumping stations | Water treatment plant and treatment processes |  |  | Energy Supply | Road Connections
Apply advanced treatment techniques (or pre-treatment) to minimize TTS/BOD: microfiltration, UV, RO, high-rate clarification | High |  | High |  |  |  |  | Expensive | Apply advanced treatment techniques (or pre-treatment) to minimize TTS/BOD: microfiltration, UV, RO, high-rate clarification |  |  | High |  |  |  |  | Expensive | Build wildfire barriers around the project |  | High | High |  |  |  | High | Expensive | Set up an emergency response plan: alert system, shut-down protocols, assignment of responsibities |  | Low | Low |  |  |  | High | Inexpensive
Elevate the concentration of biomass to maintain similar output (e.g. BOD removal) |  |  | High |  |  |  |  | Expensive | Elevate the concentration of biomass to maintain similar output (e.g. BOD removal) |  |  | High |  |  |  |  | Expensive | Install fire-detection monitoring in risk areas |  | Low | Low |  |  |  | Low | Expensive | Increase energy efficiency to allow longer operation on back-up power during emergencies |  | Low | Low |  |  |  |  | Inexpensive
Apply fouling control strategies (osmotic backwashing, enzyme cleaning, zeolites, carbon nanotubes, and graphene) |  | High | High |  |  |  |  | Expensive | Increase nutrients during cooling temepratures |  |  | High |  |  |  |  | Expensive | Prepare evacuation routes in case of a wildfire |  |  | Low |  |  |  | High | Inexpensive | Invest in n-site renewable energy to minimize dependencies on external grid |  | Low | Low |  |  | Low |  | Expensive
Use of thermoregulatory devices to maintain temperatures at optimal levels (e.g. Chiller units) |  |  | Low |  |  |  |  | Inexpensive | Insulation of exposed piping and equipment |  | Low | Low |  |  |  |  | Inexpensive | Set up a fire suppression system (water tanks, fire sprinklers, emergency firefighting equipment) or enhance the fire-fighting capacity of the facility (e.g., by increasing the water storage capacity). |  | Low | Low |  |  |  |  | Inexpensive | Establish regular inspection and maintenance protocols | [5 empty] | High |  | Inexpensive
Install UPS, power conditioning and back-up power generators |  | HIgh | High |  |  | High |  | Expensive | Install UPS, power conditioning and back-up power generators |  | High | High |  |  | High |  | Expensive | [9 empty] | Design the treatment facility in a modular manner with sufficient land available for future changes (such as extra filtration or storage capacity to support re-use of treated water for irrigation purposes) | Low | Low | Low |  |  |  |  | Inexpensive (if performed in planning phase)
Supplement aeration (e.g. by using air compressors with diffusers) |  |  | Low |  |  |  |  | Inexpensive | Install diesel pump stations to ensure the continuation of operations in case of grid blackout |  | Low | Low |  |  |  |  | Inexpensive
Perform frequent chemical cleaning to remove microrganisms |  | Low | Low |  |  |  |  | Inexpensive
Install diesel pump stations to ensure the continuation of operations in case of grid blackout |  | HIgh | [5 empty] | Inexpensive
Wastewater Treatment -Extreme Heat | [9 empty] | Wastewater Treatment - Extreme Cold | [8 empty] | Wastewater Treatment - Wildfires | [8 empty] | All-Hazards
| Sewerage networks and pumping stations | Wastewater treatment plants and processes | Receiving river body | Reuse of treated effluent for irrigation/recharge of aquifer | Land for sewage sludge spreading | Energy Supply | Road Connections |  |  | Sewerage networks and pumping stations | Wastewater treatment plants and processes | Receiving river body | Reuse of treated effluent for irrigation/recharge of aquifer | Land for sewage sludge spreading | Energy Supply | Road Connections |  |  | Sewerage networks and pumping stations | Wastewater treatment plants and processes | Receiving river body | Reuse of treated effluent for irrigation/recharge of aquifer | Land for sewage sludge spreading | Energy Supply | Road Connections |  |  | Sewerage networks and pumping stations | Wastewater treatment plants and processes | Receiving river body | Reuse of treated effluent for irrigation/recharge of aquifer | Land for sewage sludge spreading | Energy Supply | Road Connections
Apply advanced treatment techniques (or pre-treatment) to minimize TTS/BOD: microfiltration, UV, RO, high-rate clarification |  | High | High | High |  |  |  | Expensive | Apply advanced treatment techniques (or pre-treatment) to minimize TTS/BOD: microfiltration, UV, RO, high-rate clarification | [7 empty] | Expensive | Build wildfire barriers around the project | High | High |  |  |  |  | High | Expensive | Set up an emergency response plan: alert system, shut-down protocols, assignment of responsibities | Low | Low | [5 empty] | Inexpensive
Elevate the concentration of biomass to maintain similar output (e.g. BOD removal) |  | Low | Low | Low |  |  |  | Inexpensive | Elevate the concentration of biomass to maintain similar output (e.g. BOD removal) | [7 empty] | Inexpensive | Install fire-detection monitoring in risk areas | Low | Low |  |  | Low |  |  | Expensive | Increase energy efficiency to allow longer operation on back-up power during emergencies | Low | Low |  |  |  | High |  | Inexpensive
Apply fouling control strategies (osmotic backwashing, enzyme cleaning, zeolites, carbon nanotubes, and graphene) | Low | Low | [5 empty] | Inexpensive | Increase nutrients during cooling temperatures | [7 empty] | Expensive | Prepare evacuation routes in case of a wildfire |  | Low |  |  |  |  | High | Inexpensive | Invest in n-site renewable energy to minimize dependencies on external grid | [5 empty] | High |  | Expensive
Use of thermoregulatory devices to maintain temperatures at optimal levels (e.g. Chiller units) |  | Low | Low |  |  |  |  | Inexpensive | Increase influent wastewater temperatures by bleeding steam into the sewer system | [7 empty] | Expensive | Set up a fire suppression system (water tanks, fire sprinklers, emergency firefighting equipment) or enhance the fire-fighting capacity of the facility (e.g., by increasing the water storage capacity). | Low | Low | [5 empty] | Inexpensive | Establish regular inspection and maintenance protocols | Low | Low | Low | Low | Low |  |  | Inexpensive
Install UPS, power conditioning and back-up power generators | High | High |  |  |  | High |  | Expensive | Insulation of exposed piping and equipment | [7 empty] | Inexpensive | [9 empty] | Design the treatment facility in a modular manner with sufficient land available for future changes (such as extra filtration or storage capacity to support re-use of treated water for irrigation purposes) | High | High | High | High | High |  |  | Inexpensive (if performed in planning phase)
Supplement aeration (e.g. by using air compressors with diffusers) | Low | Low | [5 empty] | Inexpensive | Install UPS, power conditioning and back-up power generators | [7 empty] | Expensive
Bypass retention basins in wastewater treatment |  | Low | [5 empty] | Inexpensive | Install diesel pump stations to ensure the continuation of operations in case of grid blackout | [7 empty] | Inexpensive
Perform frequent chemical cleaning to remove microrganisms | Low | Low | [5 empty] | Inexpensive | Install storm/sewer mains below the critical freeze-thaw depth | [7 empty] | Inexpensive (if performed during planning phase)
Install diesel pump stations to ensure the continuation of operations in case of grid blackout | High | High |  |  |  | High |  | Expensive
Apply enhanced odor and corrosion control in wastewater/sewerage systems (e.g., Vapor or fan systems, chemical additions, vapor-phase control technologies etc) | High | High | [5 empty] | Expensive
Identify corrosion and odor hotspots in the sewer network to optimize planning/maintence strategies | Low | [6 empty] | Expensive
Irrigation - Extreme Heat | [8 empty] | Irrigation - Extreme Cold | [8 empty] | Irrigation - Wildfires
| Water from natural water sources | Irrigation network and pumping stations |  | Reuse of treated effluent from wastewater treatment plants |  | Energy Supply | Road Connections |  |  | Water from natural water sources | Irrigation network and pumping stations |  | Reuse of treated effluent from wastewater treatment plants |  | Energy Supply | Road Connections |  |  | Water from natural water sources | Irrigation network and pumping stations |  | Reuse of treated effluent from wastewater treatment plants |  | Energy Supply | Road Connections |  |  | Water from natural water sources | Irrigation network and pumping stations |  | Reuse of treated effluent from wastewater treatment plants |  | Energy Supply | Road Connections
Use novel materials to suppress algal growth in irrigation canals (e.g. fiberglass reinforced plastic mortar (FRPM) panels ) |  | Low | [5 empty] | Inexpensive | Insulation of exposed piping and equipment | [7 empty] | Inexpensive | Diversify options for water supply to prevent water scarcity | [7 empty] | Expensive | Set up an emergency response plan: alert system, shut-down protocols, assignment of responsibities |  | Low | [5 empty] | Inexpensive
[9 empty] | Design parabolic canals in seasonally frozen regions to benefit from their excellent hydraulic characteristics and increased frost heave resistance | [7 empty] | Inexpensive | Apply condition monitoring in water pipes (to minimize leakages and maximize water consevation) | [7 empty] | Expensive | Increase energy efficiency to allow longer operation on back-up power during emergencies |  | Low |  |  |  | High |  | Inexpensive
[9 empty] | Apply real-time water flow control to detect leakages and prevent ice build-up/ blockages during very cold days | [7 empty] | Expensive | Promote rain-harvesting practices and micro-irrigation technologies to limit water agricultural demand | [7 empty] | Inexpensive | Invest in n-site renewable energy to minimize dependencies on external grid | [5 empty] | High |  | Expensive
[18 empty] | Prepare water conservation plans (describing water metering practices, ime of day to undertake water-intensive activities) | [8 empty] | Establish regular inspection and maintenance protocols | Low | Low |  | Low |  |  |  | Inexpensive
[27 empty] | Design the treatment facility in a modular manner with sufficient land available for future changes (such as extra filtration or storage capacity to support re-use of treated water for irrigation purposes) | High | High |  | High |  |  |  | Inexpensive (if performed in planning phase)

## Soil Adaptation (hidden)
Water Facilities-Landslides | Water Facilities-Landslides | [8 empty] | Water Facilities-Saltwater | [8 empty] | All-Hazards
| Water source | Water distribution network and pumping stations | Water treatment plant and treatment processes |  |  | Energy Supply | Road Connections |  |  | Water source | Water distribution network and pumping stations | Water treatment plant and treatment processes |  |  | Energy Supply | Road Connections |  |  | Water source | Water distribution network and pumping stations | Water treatment plant and treatment processes |  |  | Energy Supply | Road Connections
Diversify options for water supply to increase the redundancies of the water facility | High | [6 empty] | Expensive | Install low-head dams across tidal estuaries to prevent saltwater intrusion | High | [6 empty] | Expensive | Implement contingency planning for loss of access routes and prolonged power shortages | [6 empty] | High | Inexpensive
Apply sediment management practices to control nutrient inputs into source water bodies | High | [6 empty] | Expensive | Inject fresh water into aquifers or Perform desalination of the abstracted brackish water and recharge the treated water into the aquifer | High | [6 empty] | Expensive | Set up an emergency response plan: alert system, shut-down protocols, assignment of responsibities |  | Low | Low |  |  |  |  | Inexpensive
Preserve or restore vegetated land covers in watersheds to manage stormwater runoff and reduce soil erosion |  |  | Low |  |  |  |  | Inexpensive | Reduce and/or rearrange the pattern of boreholes abstraction of groundwater (i.e., use boreholes near the sea during the rainy season and inland boreholes duisng the summer) | High | [6 empty] | Inexpensive | Increase energy efficiency to allow longer operation on back-up power during emergencies |  | Low | Low |  |  | Low |  | Inexpensive
Consider suitable design options for intakes that minimize sendimentation (e.g. bed intake, ubmerged intake) | High | High | [5 empty] | Inexpensive | Apply water contamination monitoring to issue automatic alerts when the quality of the influent is abnormally low |  | Low | Low |  |  |  |  | Inexpensive | Invest in n-site renewable energy to minimize dependencies on external grid | [5 empty] | High |  | Expensive
Install flushing structures in the intake to periodically flush out sediments | Low | Low | [5 empty] | Inexpensive | Apply advanced treatment techniques (or pre-treatment): microfiltration, UV, RO, high-rate clarification |  |  | High |  |  |  |  | Expensive | Establish regular inspection and maintenance protocols | Low | Low | Low |  |  |  |  | Inexpensive
Apply water contamination monitoring to issue automatic alerts when the consistency of influent in sediments/ organic matter exceeds maximum thresholds |  | Low | Low |  |  |  |  | Expensive | Apply antifouling strategies (osmotic backwashing, enzyme cleaning, zeolites, carbon nanotubes, and graphene) |  |  | High |  |  |  |  | Expensive | Design the treatment facility in a modular manner with sufficient land available for future changes (such as extra filtration or storage capacity to support re-use of treated water for irrigation purposes) | High | High | High |  |  |  |  | Inexpensive (if performed in planning phase)
Design pipeline mains to withstand large ground deformations (e.g., thicker pipelines, enhanced trenching) |  | High | [5 empty] | Expensive | Optimize pump performace to pevent or postpone clogging conditions. Prioritize special-purpose pumps that are critical to the operation of the facility. |  | Low | Low |  |  |  |  | Inexpensive
Plan bypass routes in the piping system |  | High | [5 empty] | Inexpensive (when performed in planning phase)
Incorporate easy modular extensions to the water supply network (e.g. for future additions of new water sources) | High | High | High |  |  |  |  | Inexpensive (when performed in planning phase)
Optimize pump performace to pevent or postpone clogging conditions (by iron oxide incrustationsa and sediment deposits). Prioritize special-purpose pumps that are critical to the operation of the facility. |  | Low | Low |  |  |  |  | Inexpensive
Wastewater Treatment - Landslides | [9 empty] | Wastewater Treatment - Saltwater Intrusion | [8 empty] | All-Hazards
| Sewerage networks and pumping stations | Wastewater treatment plants and processes | Receiving river body | Reuse of treated effluent for irrigation/recharge of aquifer | Land for sewage sludge spreading | Energy Supply | Road Connections |  |  | Sewerage networks and pumping stations | Wastewater treatment plants and processes | Receiving river body | Reuse of treated effluent for irrigation/recharge of aquifer | Land for sewage sludge spreading | Energy Supply | Road Connections |  |  | Sewerage networks and pumping stations | Wastewater treatment plants and processes | Receiving river body | Reuse of treated effluent for irrigation/recharge of aquifer | Land for sewage sludge spreading | Energy Supply | Road Connections
Apply advanced treatment techniques (or pre-treatment): microfiltration, UV, RO, high-rate clarification |  | High | High | High |  |  |  | Expensive | Apply contamination controls for primary and secondary water/wastewater treatment |  | High | High | High |  |  |  | Expensive | Implement contingency planning for loss of access routes and prolonged power shortages | [6 empty] | High | Inexpensive
Apply antifouling strategies (osmotic backwashing, enzyme cleaning, zeolites, carbon nanotubes, and graphene) |  | High | High | High |  |  |  | Expensive | Apply advanced treatment techniques (or pre-treatment): microfiltration, UV, RO, high-rate clarification |  | High | High | High |  |  |  | Expensive | Set up an emergency response plan: alert system, shut-down protocols, assignment of responsibities | Low | Low | [5 empty] | Inexpensive
Design pipeline mains to withstand large ground deformations (e.g., thicker pipelines, enhanced trenching) | High | [6 empty] | Inexpensive (if performed in planning phase) | Invest in high recovery, energy efficient wastewater desalination to maximize freshwater output for reverse osmosis (RO) while saving energy. |  |  | High | High |  |  |  | Expensive | Increase energy efficiency to allow longer operation on back-up power during emergencies | [5 empty] | Low |  | Inexpensive
Plan bypass routes in the piping system | High | [6 empty] | Inexpensive (if performed in planning phase) | Prioritize solutions that are suitable for treating high-salinity brine and wastewater |  |  |  | High | High |  |  | Expensive | Invest in n-site renewable energy to minimize dependencies on external grid | [5 empty] | High |  | Expensive
Apply facility-wide stromwater management to mitigate excessive run-off that intensifies soil erosion effects and triggers landlides |  | Low |  |  | Low |  |  | inexpensive | Optimize pump performace to pevent or postpone clogging conditions (by iron oxide incrustationsa and sediment deposits). Prioritize special-purpose pumps that are critical to the operation of the facility. | Low | Low | [5 empty] | Inexpensive | Establish regular inspection and maintenance protocols | Low | Low | Low | Low | Low |  |  | Inexpensive
Install field monitoring in precarious slopes and issue alerts when there is indication of landliding |  | High |  |  | High |  |  | Expensive | Apply conventional desalintion techniques for saline wastewaters |  | High | High | High |  |  |  | Expensive | Design the treatment facility in a modular manner with sufficient land available for future changes (such as extra filtration or storage capacity to support re-use of treated water for irrigation purposes) | Low | Low | Low | Low | Low |  |  | Inexpensive (when performed in planning phase)
Apply stabilization measures in unstables slopes threatening critical facilities |  | High |  |  | High |  |  | Expensive | Consider biotreatment alternatives that are environmentally friendly and less expensive |  | High | High | High |  |  |  | Expensive
Consider suitable design options for outfalls that minimize soil erosion (e.g., submerged outfall) | High |  | High |  |  |  |  | Inexpensive
Apply enhanced erosion protection on the bank side of the outfall (vegetation, riprap etc) | High |  | High |  |  |  |  | Expensive
Design mains to withstand large ground deformations (e.g., thicker pipelines, enhanced trenching) | High | [6 empty] | Expensive
Irrigation - Landslides | [8 empty] | Irrigation - Saltwater intrusion
| Water from natural water sources | Irrigation network and pumping stations |  | Reuse of treated effluent from wastewater treatment plants |  | Energy Supply | Road Connections |  |  | Water from natural water sources | Irrigation network and pumping stations |  | Reuse of treated effluent from wastewater treatment plants |  | Energy Supply | Road Connections |  |  | Water from natural water sources | Irrigation network and pumping stations |  | Reuse of treated effluent from wastewater treatment plants |  | Energy Supply | Road Connections
Plan bypass routes in the irrigation system |  | High | [5 empty] | Expensive | Reduce and/or rearrange the pattern of boreholes abstraction of groundwater (i.e., use boreholes near the sea during the rainy season and inland boreholes duisng the summer) | High | [6 empty] | Expensive | Implement contingency planning for loss of access routes and prolonged power shortages | [6 empty] | High | Inexpensive
Incorporate easy modular extensions to the supply network (e.g. for future additions of new water sources) | High |  |  | High |  |  |  | Expensive | Perform artificial aquifer recharge | High | [6 empty] | Expensive | Set up an emergency response plan: alert system, shut-down protocols, assignment of responsibities | Low | Low |  | Low |  |  |  | Inexpensive
Install field monitoring in precarious slopes and issue alerts when there is indication of landliding |  | Low | [5 empty] | Inexpensive | Perform soil salinity monitoring | Low |  |  | Low |  |  |  | Inexpensive | Increase energy efficiency to allow longer operation on back-up power during emergencies | [5 empty] | Low |  | Inexpensive
Apply soil erosion measures to unstable slopes |  | Low | [5 empty] | Inexpensive | Minimize pumping rates and make batter use of alternative water sources. | High | [6 empty] | Expensive | Invest in n-site renewable energy to minimize dependencies on external grid | [5 empty] | High |  | Expensive
[9 empty] | Perform regular measurements of the irrigation water quality (i electrical conductivity, Ecw, water sodicity) | Low | Low |  | Low |  |  |  | Inexpensive | Establish regular inspection and maintenance protocols | Low | Low |  | Low |  |  |  | Inexpensive
[9 empty] | Plant high-tolerant crops that can better adopt to saline environements | Low | Low |  | Low |  |  |  | Inexpensive | Design the treatment facility in a modular manner with sufficient land available for future changes (such as extra filtration or storage capacity to support re-use of treated water for irrigation purposes) | Low | Low |  | Low |  |  |  | Inexpensive (when performed in planning phase)
[9 empty] | Replace surface irrigation with drip irrigation systems which are more appropriate for salt sensitive soils. |  | Low | [5 empty] | Inexpensive
[9 empty] | Optimize irrigation scheduling to eliminate salinity-build-up in the root zone of plants (e.g., Small/frequent intervals for dip irrigation systems, large/less frequent intervals for surface irrigation) |  | Low | [5 empty] | Inexpensive
[9 empty] | Optimize the design of drainage infrastructure to minimize salts accumulation in root-zone. |  | Low | [5 empty] | Inexpensive
[9 empty] | Consider a change in the land use if the salinity threat cannot be mitigated | High | High |  | High |  |  |  | Expensive
|  | Water source | Water distribution network and pumping stations
High
High
Low
|  | High | High
|  | Low | Low
|  |  | Low | Low
High
High
|  | High | High | High
|  |  | Low | Low

## Wind Adaptation (hidden)
Water Facilities-Landslides | Water Facilities-Landslides | [8 empty] | Water Facilities-Saltwater | [8 empty] | All-Hazards
| Water source | Water distribution network and pumping stations | Water treatment plant and treatment processes |  |  | Energy Supply | Road Connections |  |  | Water source | Water distribution network and pumping stations | Water treatment plant and treatment processes |  |  | Energy Supply | Road Connections |  |  | Water source | Water distribution network and pumping stations | Water treatment plant and treatment processes |  |  | Energy Supply | Road Connections
Install alert systems for extreme weather events providing warnings ahead of the the impeding storm. |  | Low | Low |  |  |  |  | Expensive | Install low-head dams across tidal estuaries to prevent saltwater intrusion | High | [6 empty] | Expensive | Implement contingency planning for loss of access routes and prolonged power shortages | [6 empty] | High | Inexpensive
Replace elevated tanks with ground-based (where possible). |  |  | High |  |  |  |  | Expensive | Inject fresh water into aquifers or Perform desalination of the abstracted brackish water and recharge the treated water into the aquifer | High | [6 empty] | Expensive | Set up an emergency response plan: alert system, shut-down protocols, assignment of responsibities |  | Low | Low |  |  |  |  | Inexpensive
Install wind-proof shelter to protect materials and sensitive equipment from adverse weather conditions |  |  | Low |  |  |  |  | Inexpensive | Reduce and/or rearrange the pattern of boreholes abstraction of groundwater (i.e., use boreholes near the sea during the rainy season and inland boreholes duisng the summer) | High | [6 empty] | Inexpensive | Increase energy efficiency to allow longer operation on back-up power during emergencies |  | Low | Low |  |  | Low |  | Inexpensive
Upgrade steel connections using advanced bolting solutions |  |  | Low |  |  |  |  | Inexpensive | Apply water contamination monitoring to issue automatic alerts when the quality of the influent is abnormally low |  | Low | Low |  |  |  |  | Inexpensive | Invest in n-site renewable energy to minimize dependencies on external grid | [5 empty] | High |  | Expensive
Cover up/Shelter treatment processes to protect containment from flying dust, objects etc. |  |  | Low |  |  |  |  | Inexpensive | Apply advanced treatment techniques (or pre-treatment): microfiltration, UV, RO, high-rate clarification |  |  | High |  |  |  |  | Expensive | Establish regular inspection and maintenance protocols | Low | Low | Low |  |  |  |  | Inexpensive
Reinforce lighting protection |  | Low | Low |  |  |  |  | Inexpensive | Apply antifouling strategies (osmotic backwashing, enzyme cleaning, zeolites, carbon nanotubes, and graphene) |  |  | High |  |  |  |  | Expensive | Design the treatment facility in a modular manner with sufficient land available for future changes (such as extra filtration or storage capacity to support re-use of treated water for irrigation purposes) | High | High | High |  |  |  |  | Inexpensive (if performed in planning phase)
Install UPS, power conditioning and back-up power generators |  |  | High |  |  | High |  | Expensive | Optimize pump performace to pevent or postpone clogging conditions. Prioritize special-purpose pumps that are critical to the operation of the facility. |  | Low | Low |  |  |  |  | Inexpensive
Install diesel pump stations to ensure the continuation of operations in case of grid blackout |  | Low |  |  |  | Low |  | Inexpensive
Wastewater Treatment - Landslides | [9 empty] | Wastewater Treatment - Saltwater Intrusion | [8 empty] | All-Hazards
| Sewerage networks and pumping stations | Wastewater treatment plants and processes | Receiving river body | Reuse of treated effluent for irrigation/recharge of aquifer | Land for sewage sludge spreading | Energy Supply | Road Connections |  |  | Sewerage networks and pumping stations | Wastewater treatment plants and processes | Receiving river body | Reuse of treated effluent for irrigation/recharge of aquifer | Land for sewage sludge spreading | Energy Supply | Road Connections |  |  | Sewerage networks and pumping stations | Wastewater treatment plants and processes | Receiving river body | Reuse of treated effluent for irrigation/recharge of aquifer | Land for sewage sludge spreading | Energy Supply | Road Connections
Install alert systems for extreme weather events providing warnings ahead of the the impeding storm. | Low | Low | [5 empty] | Expensive | Apply contamination controls for primary and secondary water/wastewater treatment |  | High | High | High |  |  |  | Expensive | Implement contingency planning for loss of access routes and prolonged power shortages | [6 empty] | High | Inexpensive
Replace elevated tanks with ground-based (where possible). |  | High | [5 empty] | Expensive | Apply advanced treatment techniques (or pre-treatment): microfiltration, UV, RO, high-rate clarification |  | High | High | High |  |  |  | Expensive | Set up an emergency response plan: alert system, shut-down protocols, assignment of responsibities | Low | Low | [5 empty] | Inexpensive
Install wind-proof shelter to protect materials and sensitive equipment from adverse weather conditions |  | Low | [5 empty] | Inexpensive | Invest in high recovery, energy efficient wastewater desalination to maximize freshwater output for reverse osmosis (RO) while saving energy. |  |  | High | High |  |  |  | Expensive | Increase energy efficiency to allow longer operation on back-up power during emergencies | [5 empty] | Low |  | Inexpensive
Upgrade steel connections using advanced bolting solutions |  | Low | [5 empty] | Inexpensive | Prioritize solutions that are suitable for treating high-salinity brine and wastewater |  |  |  | High | High |  |  | Expensive | Invest in n-site renewable energy to minimize dependencies on external grid | [5 empty] | High |  | Expensive
Cover up/Shelter treatment processes to protect containment from flying dust, objects etc. |  | Low | [5 empty] | Inexpensive | Optimize pump performace to pevent or postpone clogging conditions (by iron oxide incrustationsa and sediment deposits). Prioritize special-purpose pumps that are critical to the operation of the facility. | Low | Low | [5 empty] | Inexpensive | Establish regular inspection and maintenance protocols | Low | Low | Low | Low | Low |  |  | Inexpensive
Reinforce lighting protection | Low | [6 empty] | Expensive | Apply conventional desalintion techniques for saline wastewaters |  | High | High | High |  |  |  | Expensive | Design the treatment facility in a modular manner with sufficient land available for future changes (such as extra filtration or storage capacity to support re-use of treated water for irrigation purposes) | Low | Low | Low | Low | Low |  |  | Inexpensive (when performed in planning phase)
Install UPS, power conditioning and back-up power generators |  | Low |  |  |  | High |  | Expensive | Consider biotreatment alternatives that are environmentally friendly and less expensive |  | High | High | High |  |  |  | Expensive
Install diesel pump stations to ensure the continuation of operations in case of grid blackout | Low |  |  |  |  | Low |  | Inexpensive
Irrigation - Landslides | [8 empty] | Irrigation - Saltwater intrusion
| Water from natural water sources | Irrigation network and pumping stations |  | Reuse of treated effluent from wastewater treatment plants |  | Energy Supply | Road Connections |  |  | Water from natural water sources | Irrigation network and pumping stations |  | Reuse of treated effluent from wastewater treatment plants |  | Energy Supply | Road Connections |  |  | Water from natural water sources | Irrigation network and pumping stations |  | Reuse of treated effluent from wastewater treatment plants |  | Energy Supply | Road Connections
Install alert systems for extreme weather events providing warnings ahead of the the impeding storm. |  | Low | [5 empty] | Inexpensive | Reduce and/or rearrange the pattern of boreholes abstraction of groundwater (i.e., use boreholes near the sea during the rainy season and inland boreholes duisng the summer) | High | [6 empty] | Expensive | Implement contingency planning for loss of access routes and prolonged power shortages | [6 empty] | High | Inexpensive
Install wind-proof shelter to protect materials and sensitive equipment from adverse weather conditions |  | Low | [5 empty] | Inexpensive | Perform artificial aquifer recharge | High | [6 empty] | Expensive | Set up an emergency response plan: alert system, shut-down protocols, assignment of responsibities | Low | Low |  | Low |  |  |  | Inexpensive
Install UPS, power conditioning and back-up power generators | [5 empty] | High |  | Expensive | Perform soil salinity monitoring | Low |  |  | Low |  |  |  | Inexpensive | Increase energy efficiency to allow longer operation on back-up power during emergencies | [5 empty] | Low |  | Inexpensive
[9 empty] | Minimize pumping rates and make batter use of alternative water sources. | High | [6 empty] | Expensive | Invest in n-site renewable energy to minimize dependencies on external grid | [5 empty] | High |  | Expensive
[9 empty] | Perform regular measurements of the irrigation water quality (i electrical conductivity, Ecw, water sodicity) | Low | Low |  | Low |  |  |  | Inexpensive | Establish regular inspection and maintenance protocols | Low | Low |  | Low |  |  |  | Inexpensive
[9 empty] | Plant high-tolerant crops that can better adopt to saline environements | Low | Low |  | Low |  |  |  | Inexpensive | Design the treatment facility in a modular manner with sufficient land available for future changes (such as extra filtration or storage capacity to support re-use of treated water for irrigation purposes) | Low | Low |  | Low |  |  |  | Inexpensive (when performed in planning phase)
[9 empty] | Replace surface irrigation with drip irrigation systems which are more appropriate for salt sensitive soils. |  | Low | [5 empty] | Inexpensive
[9 empty] | Optimize irrigation scheduling to eliminate salinity-build-up in the root zone of plants (e.g., Small/frequent intervals for dip irrigation systems, large/less frequent intervals for surface irrigation) |  | Low | [5 empty] | Inexpensive
[9 empty] | Optimize the design of drainage infrastructure to minimize salts accumulation in root-zone. |  | Low | [5 empty] | Inexpensive
[9 empty] | Consider a change in the land use if the salinity threat cannot be mitigated | High | High |  | High |  |  |  | Expensive
|  | Water source | Water distribution network and pumping stations
High
High
Low
|  | High | High
|  | Low | Low
|  |  | Low | Low
High
High
|  | High | High | High
|  |  | Low | Low